## README
PROJECT 2 - FULL ELECTRICAL PACKAGE
Northfield Raw Water Pump Station - MCC-01
SELF-DIRECTED REFERENCE PROJECT - NOT DELIVERED WORK.
The scenario and client are fictional. The engineering workflow and failure modes are real.
PART NUMBERS ARE INDICATIVE. Several will be wrong. Catalogue numbers change, accessories get
missed, and coil/curve/pole variants are the most commonly botched field in any switchboard BOM.
Every part number must be verified against the manufacturer's current catalogue and confirmed on
the vendor quotation before a purchase order is raised.
NOT PERFORMED AND NOT CLAIMED: fault level study, protection coordination study, protection
settings, arc flash study, AS/NZS 3008 cable calculations, functional safety PL determination or
verification, AS/NZS 61439 design verification (that is the assembly manufacturer's responsibility).
SHEETS
Design Input Register — 26 rows
TQ Register — 11 rows
IO List — 124 rows
Cable Schedule — 32 rows
Termination Schedule — 236 rows
BOM — 105 rows
FAT Sheet — 139 rows
Punch List — 8 rows
Inspection Checklist — 62 rows
MDR Index — 49 rows

## Design Input Register
ID | Requirement | Source | Engineering Response | Drawing/Document Affected | Status | Owner to Close
DI-001 | Supply 415 V 3ph 4W 50 Hz from TX-01 | Client drawing NFD-CLI-SLD-9001 | Adopted as design supply. Incomer 4-pole to break neutral. | SLD-0001 | Closed | -
DI-002 | Transformer 500 kVA Dyn11 Z=5% | TX-01 nameplate (photo on file) | Used for indicative fault contribution only. Not accepted as design fault level. | DBS-0001 | Closed | -
DI-003 | Prospective fault level at MCC | NOT SUPPLIED | 25 kA / 1 s ASSUMED for tender. All breaker Icu/Ics and busbar Icw provisional. Must be confirmed before design freeze. | SLD-0001, BOM | OPEN - TQ-002 | Client / network operator
DI-004 | Earthing system (TN-S / TN-C-S) | NOT SUPPLIED | TN-S assumed. Separate N and E bars. Earth-fault element provisioned at incomer. | SLD-0001 | OPEN - TQ-001 | Client
DI-005 | Client Electrical Design Standard | NOT SUPPLIED | Generic industry practice adopted as interim basis. Substantial rework risk if client standard differs. | All | Closed Wk11 - TQ-001 | Client
DI-006 | Two transfer pumps 75 kW variable speed duty/assist | Client functional spec 4.2 | Two VSD feeders. Duty rotation and assist logic in functional description. | SLD-0001, SCH-0101/0111, FDS | Superseded by DI-024 | -
DI-007 | Pump motor full nameplate data | Pump vendor - NOT ISSUED | Typical 4-pole figures used for frame selection only. Drive, breaker, cable and thermal data cannot be finalised without it. | SLD, BOM, cable schedule | Closed Wk13 (90 kW) | Pump vendor
DI-008 | Drive must accept motor PTC thermistors | Design decision | Independent thermistor relay per pump. Trip wired to drive external fault and to PLC. | SCH-0101, BOM | Closed | -
DI-009 | Dry-run protection required | Client functional spec 4.6 | Independent low-low float hardwired into stop logic in addition to PLC level control. | SCH-0101, SCH-0201 | Closed | -
DI-010 | Emergency stop at each pump and at MCC | Client functional spec 6.1 | Dual-channel monitored E-stop, safety relay, STO to drives, coil drop to DOL feeders, monitored manual reset. | SCH-0040 | Closed (architecture) | -
DI-011 | Required Performance Level for E-stop safety function | NOT SUPPLIED | PLd architecture adopted as interim. Required PL requires machinery risk assessment; achieved PL requires ISO 13849-1 calculation. NEITHER PERFORMED BY US. | SCH-0040, BOM | OPEN - TQ-003 | Client / safety consultant
DI-012 | Local control station at each pump | Client functional spec 6.2 | LCS-101/102: L-O-R selector, Start, Stop, E-stop, Running lamp. IP66 GRP. | SCH-0101, TRM-0401 | Closed | -
DI-013 | Indoor air-conditioned switchroom | Site visit report | IP42 adopted. Anti-condensation heaters with hygrostat as insurance against HVAC outage. | DBS, BOM | Closed | -
DI-014 | MCC operation with HVAC failed | NOT STATED | Two options priced: (a) uprate/derate for 50 C, (b) HVAC-fail interlock ramping drives down. | DBS, SCH-0201, BOM | Closed Wk7 - option (b) | Client
DI-015 | Declared heat load to HVAC designer | Interface requirement | Estimated total dissipation issued in writing at Rev B. Reissued at Rev 1 after motor uprate. | IFM-002 | Closed (reissued) | -
DI-016 | PLC platform and I/O standard | NOT SUPPLIED | CompactLogix 5380 assumed. Module selection, spares and SCADA driver all depend on this. | SLD, BOM, I/O list | Closed Wk9 - TQ-007 | Client
DI-017 | IP address schedule | NOT SUPPLIED | Placeholder scheme used for FAT only. Must be replaced before site. | Network drawing, FAT | Closed Wk9 | Client
DI-018 | SCADA communication over existing plant fibre | Client functional spec 8 | Managed switch with multimode fibre ports. One to control room, one to RIO-01. | SLD, BOM | Closed (see DR-004) | -
DI-019 | Remote I/O at intake screen approx 120 m | Site layout drawing | RIO-01 with EtherNet/IP adapter and fibre link. Separate 240 V supply at kiosk with own 24 V PSU. | SLD, RIO drawings | Closed | -
DI-020 | Harmonic distortion limits at point of connection | NOT SUPPLIED | Two six-pulse drives on a 500 kVA transformer warrants assessment. Provisional line reactors; active filter carried as risk. | SLD, BOM, GA | OPEN - TQ-006 | Client / specialist
DI-021 | Spare capacity requirement | NOT STATED | 20% spare terminals, 20% spare I/O, two fitted spare feeders, 20% spare chassis. | All | Closed Wk11 - TQ-001 | Client
DI-022 | Surge protection required | Client functional spec 5.4 | Type 1+2 SPD at incomer on dedicated protective device, status contact to PLC. | SLD, SCH-0201 | Closed | -
DI-023 | Cable entry direction | NOT SUPPLIED | Top entry assumed. GA cannot be released until confirmed. | GA, gland plate detail | Closed Wk11 - TQ-001 | Client
DI-024 | REVISED PUMP DUTY - motors uprated 75 kW to 90 kW | Client TQ response TQR-009 after hydraulic re-modelling | Full change impact assessment raised. See CR-001 / Stage 9. | SLD, SCH-0101/0111, TRM, BOM, GA, cable schedule, FAT, heat load | Closed Wk14 - implemented Rev 1 | -
DI-025 | Seal water flow proving on each pump | Client functional spec 4.7 | Flow switch per pump wired as start permissive with run-delay bypass. | SCH-0101, SCH-0201 | Closed | -
DI-026 | TX-01 transformer capacity with revised MCC demand plus existing site loads | Raised by us following CR-001 | Revised MCC demand ~447 A against 500 kVA (~695 A). TX-01 also feeds site loads outside our scope. Client must confirm total. | DBS, carried-forward register | OPEN - TQ-011 | Client

## TQ Register
TQ No. | Subject | Raised (Wk) | Required By (Wk) | Assumption Stated | Impact If Unanswered | Owner | Status
TQ-001 | Client Electrical Design Standard. Covers earthing system, form of separation, cable entry direction, spare capacity, wire numbering convention, drive brand standard. | 1 | 3 | Generic industry practice, TN-S, Form 3b, top entry, 20% spares | Blocks enclosure fabrication release. Six assumptions depend on it. | Client | Closed Wk11
TQ-002 | Prospective short-circuit current at MCC incomer and expected duration. | 1 | 4 | 25 kA for 1 s | Blocks all MCCB and busbar orders. Highest cost exposure in the package. | Client / network operator | OPEN - escalated x2
TQ-003 | Required Performance Level for E-stop safety function, and required stop category (0 or 1) given hydraulic surge considerations. | 2 | 6 | PLd architecture, Category 0 | Blocks safety relay order; may change safety circuit architecture. | Client / safety consultant | OPEN
TQ-004 | Who is performing the protection coordination study and when will settings be available? | 2 | 10 | Provisional conservative settings | Settings cannot be applied or recorded at FAT. | Client | OPEN - see FD-005
TQ-005 | Must the MCC operate with switchroom HVAC failed? Two options priced. | 2 | 5 | 40 C design ambient with HVAC operating | Changes derating basis, possibly drive frame size, or adds control interlock. | Client | Closed Wk7 - interlock selected
TQ-006 | Harmonic distortion limits at point of connection. Is a harmonic assessment being performed? | 3 | 6 | Line reactors sufficient | May require active harmonic filter - additional cubicle, cost, 12+ wk lead. | Client | OPEN - highest technical risk
TQ-007 | PLC platform standard and IP address schedule. | 1 | 4 | CompactLogix 5380 | Blocks all PLC hardware orders. | Client | Closed Wk9
TQ-008 | Motor nameplate data for P-101 / P-102. | 2 | 6 | Typical 4-pole values | Blocks drive, feeder breaker, cable and thermal settings. | Pump vendor | Superseded by TQ-009
TQ-009 | Revised pump duty - hydraulic re-modelling indicates 90 kW motors required. Confirm and issue nameplate data. | 12 | 13 | - | Major change - see CR-001. | Client / pump vendor | Closed Wk13
TQ-010 | MOV-101 actuator control interface - hardwired, analogue or fieldbus? Wiring diagram required. | 3 | 7 | Hardwired open/close/stop | Schematic and terminal count cannot be finalised. | Valve vendor | Closed Wk8
TQ-011 | TX-01 transformer capacity with revised MCC demand plus existing site loads not in our scope. | 13 | 15 | Adequate | Potential transformer replacement - six figures, long lead, outage. | Client | OPEN - carried to site

## IO List
Point | Type | Module | Slot | Channel | Tag | Description | Signal | Fail-Safe | Terminal | Cable | Drawing Ref
DI-00 | DI | 5069-IB16 | 2 | 0 | Q11-AUX | Q11 MCCB auxiliary - feeder available | 24 VDC | NC | X3:020 | - | SCH-0201
DI-01 | DI | 5069-IB16 | 2 | 1 | VSD-101 | Drive healthy / ready | 24 VDC | NC | X3:017 | - | SCH-0201
DI-02 | DI | 5069-IB16 | 2 | 2 | VSD-101 | Drive running feedback | 24 VDC | NO | X3:018 | - | SCH-0201
DI-03 | DI | 5069-IB16 | 2 | 3 | S101-LOR | L-O-R selector, Local position | 24 VDC | NO | X3:005 | C-0102 | SCH-0201
DI-04 | DI | 5069-IB16 | 2 | 4 | S101-LOR | L-O-R selector, Remote position | 24 VDC | NO | X3:006 | C-0102 | SCH-0201
DI-05 | DI | 5069-IB16 | 2 | 5 | KT101 | PTC thermistor relay healthy | 24 VDC | NC | X3:013 | C-0103 | SCH-0201
DI-06 | DI | 5069-IB16 | 2 | 6 | B101-SEAL | Seal water flow proven | 24 VDC | NC | X3:015 | C-0104 | SCH-0201
DI-07 | DI | 5069-IB16 | 2 | 7 | Q12-AUX | Q12 MCCB auxiliary - feeder available | 24 VDC | NC | X3:050 | - | SCH-0201
DI-08 | DI | 5069-IB16 | 2 | 8 | VSD-102 | Drive healthy / ready | 24 VDC | NC | X3:047 | - | SCH-0201
DI-09 | DI | 5069-IB16 | 2 | 9 | VSD-102 | Drive running feedback | 24 VDC | NO | X3:048 | - | SCH-0201
DI-10 | DI | 5069-IB16 | 2 | 10 | S102-LOR | L-O-R selector, Local position | 24 VDC | NO | X3:035 | C-0112 | SCH-0201
DI-11 | DI | 5069-IB16 | 2 | 11 | S102-LOR | L-O-R selector, Remote position | 24 VDC | NO | X3:036 | C-0112 | SCH-0201
DI-12 | DI | 5069-IB16 | 2 | 12 | KT102 | PTC thermistor relay healthy | 24 VDC | NC | X3:043 | C-0113 | SCH-0201
DI-13 | DI | 5069-IB16 | 2 | 13 | B102-SEAL | Seal water flow proven | 24 VDC | NC | X3:045 | C-0114 | SCH-0201
DI-14 | DI | 5069-IB16 | 2 | 14 | - | Spare digital input | 24 VDC | - | X3:031 | - | SCH-0201
DI-15 | DI | 5069-IB16 | 2 | 15 | - | Spare digital input | 24 VDC | - | X3:032 | - | SCH-0201
DI-16 | DI | 5069-IB16 | 3 | 0 | Q15-AUX | MPCB auxiliary - feeder available | 24 VDC | NC | X3:061 | - | SCH-0201
DI-17 | DI | 5069-IB16 | 3 | 1 | KM103 | Contactor auxiliary - running (NOT the DO echo) | 24 VDC | NO | X3:062 | - | SCH-0201
DI-18 | DI | 5069-IB16 | 3 | 2 | S103-LOR | L-O-R selector, Local position | 24 VDC | NO | X3:063 | - | SCH-0201
DI-19 | DI | 5069-IB16 | 3 | 3 | S103-LOR | L-O-R selector, Remote position | 24 VDC | NO | X3:064 | - | SCH-0201
DI-20 | DI | 5069-IB16 | 3 | 4 | LSH-103 | Sump high level float - start | 24 VDC | NO | X3:065 | C-0122 | SCH-0201
DI-21 | DI | 5069-IB16 | 3 | 5 | LSL-103 | Sump low level float - stop | 24 VDC | NC | X3:066 | C-0122 | SCH-0201
DI-22 | DI | 5069-IB16 | 3 | 6 | Q16-AUX | MPCB auxiliary - feeder available | 24 VDC | NC | X3:071 | - | SCH-0201
DI-23 | DI | 5069-IB16 | 3 | 7 | KM101C | Contactor auxiliary - running | 24 VDC | NO | X3:072 | - | SCH-0201
DI-24 | DI | 5069-IB16 | 3 | 8 | PSL-101 | Instrument air pressure low - start demand | 24 VDC | NO | X3:073 | C-0132 | SCH-0201
DI-25 | DI | 5069-IB16 | 3 | 9 | ZSO-101 | Valve open limit switch | 24 VDC | NO | X3:081 | C-0142 | SCH-0201
DI-26 | DI | 5069-IB16 | 3 | 10 | ZSC-101 | Valve closed limit switch | 24 VDC | NO | X3:082 | C-0142 | SCH-0201
DI-27 | DI | 5069-IB16 | 3 | 11 | MOV-101 | Actuator fault (vendor contact) | 24 VDC | NC | X3:083 | C-0142 | SCH-0201
DI-28 | DI | 5069-IB16 | 3 | 12 | MOV-101 | Actuator in remote (vendor contact) | 24 VDC | NO | X3:084 | C-0142 | SCH-0201
DI-29 | DI | 5069-IB16 | 3 | 13 | HVAC-01 | Switchroom HVAC fault - drives ramp to min speed | 24 VDC | NC | X3:091 | C-0503 | SCH-0201
DI-30 | DI | 5069-IB16 | 3 | 14 | - | Spare digital input | 24 VDC | - | X3:092 | - | SCH-0201
DI-31 | DI | 5069-IB16 | 3 | 15 | - | Spare digital input | 24 VDC | - | X3:093 | - | SCH-0201
DI-32 | DI | 5069-IB16 | 4 | 0 | KS-01 | Safety relay auxiliary - E-stop circuit healthy | 24 VDC | NC | X3:101 | - | SCH-0202
DI-33 | DI | 5069-IB16 | 4 | 1 | Q1-OF | Incomer status | 24 VDC | NO | X3:102 | - | SCH-0202
DI-34 | DI | 5069-IB16 | 4 | 2 | Q1-SD | Incomer trip indication (separate alarm to status) | 24 VDC | NO | X3:103 | - | SCH-0202
DI-35 | DI | 5069-IB16 | 4 | 3 | KVP-01 | Phase failure / sequence relay healthy | 24 VDC | NC | X3:104 | - | SCH-0202
DI-36 | DI | 5069-IB16 | 4 | 4 | SPD-01 | Surge protective device status | 24 VDC | NC | X3:105 | - | SCH-0202
DI-37 | DI | 5069-IB16 | 4 | 5 | PSU-1 | 24 VDC PSU 1 healthy | 24 VDC | NC | X3:106 | - | SCH-0202
DI-38 | DI | 5069-IB16 | 4 | 6 | PSU-2 | 24 VDC PSU 2 healthy | 24 VDC | NC | X3:107 | - | SCH-0202
DI-39 | DI | 5069-IB16 | 4 | 7 | UPS-01 | UPS on battery - supply fail imminent | 24 VDC | NO | X3:108 | - | SCH-0202
DI-40 | DI | 5069-IB16 | 4 | 8 | UPS-01 | UPS internal fault | 24 VDC | NO | X3:109 | - | SCH-0202
DI-41 | DI | 5069-IB16 | 4 | 9 | ECP1-6 | Any 24 VDC circuit protector tripped (common) | 24 VDC | NC | X3:110 | - | SCH-0202
DI-42 | DI | 5069-IB16 | 4 | 10 | LSLL-101 | Wet well low-low float - HARDWIRED dry-run trip, also monitored | 24 VDC | NC | X3:021 | C-0210 | SCH-0202
DI-43 | DI | 5069-IB16 | 4 | 11 | LSHH-101 | Wet well high-high float | 24 VDC | NC | X3:111 | C-0211 | SCH-0202
DI-44 | DI | 5069-IB16 | 4 | 12 | - | Spare digital input | 24 VDC | - | X3:112 | - | SCH-0202
DI-45 | DI | 5069-IB16 | 4 | 13 | - | Spare digital input | 24 VDC | - | X3:113 | - | SCH-0202
DI-46 | DI | 5069-IB16 | 4 | 14 | - | Spare digital input | 24 VDC | - | X3:114 | - | SCH-0202
DI-47 | DI | 5069-IB16 | 4 | 15 | - | Spare digital input | 24 VDC | - | X3:115 | - | SCH-0202
DO-00 | DO | 5069-OB16 | 5 | 0 | KA101 | P-101 Run command to VSD-101 via interposing relay | 24 VDC | - | X3:019 | - | SCH-0202
DO-01 | DO | 5069-OB16 | 5 | 1 | VSD-101 | P-101 Fault reset to drive | 24 VDC | - | X3:023 | - | SCH-0202
DO-02 | DO | 5069-OB16 | 5 | 2 | KA102 | P-102 Run command to VSD-102 via interposing relay | 24 VDC | - | X3:049 | - | SCH-0202
DO-03 | DO | 5069-OB16 | 5 | 3 | VSD-102 | P-102 Fault reset to drive | 24 VDC | - | X3:053 | - | SCH-0202
DO-04 | DO | 5069-OB16 | 5 | 4 | KM103 | P-103 sump pump start | 24 VDC | - | X3:067 | - | SCH-0202
DO-05 | DO | 5069-OB16 | 5 | 5 | KM101C | C-101 compressor start | 24 VDC | - | X3:074 | - | SCH-0202
DO-06 | DO | 5069-OB16 | 5 | 6 | MOV-101 | MOV-101 open command | 24 VDC | - | X3:085 | C-0142 | SCH-0202
DO-07 | DO | 5069-OB16 | 5 | 7 | MOV-101 | MOV-101 close command | 24 VDC | - | X3:086 | C-0142 | SCH-0202
DO-08 | DO | 5069-OB16 | 5 | 8 | MOV-101 | MOV-101 stop command | 24 VDC | - | X3:087 | C-0142 | SCH-0202
DO-09 | DO | 5069-OB16 | 5 | 9 | HA-01 | Common alarm beacon | 24 VDC | - | X3:121 | - | SCH-0202
DO-10 | DO | 5069-OB16 | 5 | 10 | HA-02 | Common alarm sounder | 24 VDC | - | X3:122 | - | SCH-0202
DO-11 | DO | 5069-OB16 | 5 | 11 | SCADA | Station healthy watchdog to SCADA | 24 VDC | - | X3:123 | - | SCH-0202
DO-12 | DO | 5069-OB16 | 5 | 12 | VSD-101 | P-101 drive remote reference enable | 24 VDC | - | X3:024 | - | SCH-0202
DO-13 | DO | 5069-OB16 | 5 | 13 | VSD-102 | P-102 drive remote reference enable | 24 VDC | - | X3:054 | - | SCH-0202
DO-14 | DO | 5069-OB16 | 5 | 14 | - | Spare digital output | 24 VDC | - | X3:130 | - | SCH-0202
DO-15 | DO | 5069-OB16 | 5 | 15 | - | Spare digital output | 24 VDC | - | X3:131 | - | SCH-0202
DO-16 | DO | 5069-OB16 | 6 | 0 | - | Spare digital output | 24 VDC | - | X3:132 | - | SCH-0202
DO-17 | DO | 5069-OB16 | 6 | 1 | - | Spare digital output | 24 VDC | - | X3:133 | - | SCH-0202
DO-18 | DO | 5069-OB16 | 6 | 2 | - | Spare digital output | 24 VDC | - | X3:134 | - | SCH-0202
DO-19 | DO | 5069-OB16 | 6 | 3 | - | Spare digital output | 24 VDC | - | X3:135 | - | SCH-0202
DO-20 | DO | 5069-OB16 | 6 | 4 | - | Spare digital output | 24 VDC | - | X3:136 | - | SCH-0202
DO-21 | DO | 5069-OB16 | 6 | 5 | - | Spare digital output | 24 VDC | - | X3:137 | - | SCH-0202
DO-22 | DO | 5069-OB16 | 6 | 6 | - | Spare digital output | 24 VDC | - | X3:138 | - | SCH-0202
DO-23 | DO | 5069-OB16 | 6 | 7 | - | Spare digital output | 24 VDC | - | X3:139 | - | SCH-0202
DO-24 | DO | 5069-OB16 | 6 | 8 | - | Spare digital output | 24 VDC | - | X3:140 | - | SCH-0202
DO-25 | DO | 5069-OB16 | 6 | 9 | - | Spare digital output | 24 VDC | - | X3:141 | - | SCH-0202
DO-26 | DO | 5069-OB16 | 6 | 10 | - | Spare digital output | 24 VDC | - | X3:142 | - | SCH-0202
DO-27 | DO | 5069-OB16 | 6 | 11 | - | Spare digital output | 24 VDC | - | X3:143 | - | SCH-0202
DO-28 | DO | 5069-OB16 | 6 | 12 | - | Spare digital output | 24 VDC | - | X3:144 | - | SCH-0202
DO-29 | DO | 5069-OB16 | 6 | 13 | - | Spare digital output | 24 VDC | - | X3:145 | - | SCH-0202
DO-30 | DO | 5069-OB16 | 6 | 14 | - | Spare digital output | 24 VDC | - | X3:146 | - | SCH-0202
DO-31 | DO | 5069-OB16 | 6 | 15 | - | Spare digital output | 24 VDC | - | X3:147 | - | SCH-0202
AI-00 | AI | 5069-IF8 | 7 | 0 | LIT-101 | Wet well level (0-10 m) | 4-20 mA | Live zero | X4:001/002 | C-0201 | SCH-0203
AI-01 | AI | 5069-IF8 | 7 | 1 | FIT-101 | Discharge flow (0-200 L/s) | 4-20 mA | Live zero | X4:003/004 | C-0202 | SCH-0203
AI-02 | AI | 5069-IF8 | 7 | 2 | PIT-101 | P-101 discharge pressure (0-1000 kPa) | 4-20 mA | Live zero | X4:005/006 | C-0203 | SCH-0203
AI-03 | AI | 5069-IF8 | 7 | 3 | PIT-102 | P-102 discharge pressure (0-1000 kPa) | 4-20 mA | Live zero | X4:007/008 | C-0204 | SCH-0203
AI-04 | AI | 5069-IF8 | 7 | 4 | PIT-103 | Common suction pressure (0-600 kPa) | 4-20 mA | Live zero | X4:009/010 | C-0205 | SCH-0203
AI-05 | AI | 5069-IF8 | 7 | 5 | AIT-101 | Raw water turbidity (0-100 NTU) | 4-20 mA | Live zero | X4:011/012 | C-0206 | SCH-0203
AI-06 | AI | 5069-IF8 | 7 | 6 | - | Spare analogue input | 4-20 mA | Live zero | X4:013 | - | SCH-0203
AI-07 | AI | 5069-IF8 | 7 | 7 | - | Spare analogue input | 4-20 mA | Live zero | X4:015 | - | SCH-0203
AI-08 | AI | 5069-IF8 | 8 | 0 | - | Spare analogue input | 4-20 mA | Live zero | X4:017 | - | SCH-0203
AI-09 | AI | 5069-IF8 | 8 | 1 | - | Spare analogue input | 4-20 mA | Live zero | X4:019 | - | SCH-0203
AI-10 | AI | 5069-IF8 | 8 | 2 | - | Spare analogue input | 4-20 mA | Live zero | X4:021 | - | SCH-0203
AI-11 | AI | 5069-IF8 | 8 | 3 | - | Spare analogue input | 4-20 mA | Live zero | X4:023 | - | SCH-0203
AI-12 | AI | 5069-IF8 | 8 | 4 | - | Spare analogue input | 4-20 mA | Live zero | X4:025 | - | SCH-0203
AI-13 | AI | 5069-IF8 | 8 | 5 | - | Spare analogue input | 4-20 mA | Live zero | X4:027 | - | SCH-0203
AI-14 | AI | 5069-IF8 | 8 | 6 | - | Spare analogue input | 4-20 mA | Live zero | X4:029 | - | SCH-0203
AI-15 | AI | 5069-IF8 | 8 | 7 | - | Spare analogue input | 4-20 mA | Live zero | X4:031 | - | SCH-0203
AO-00 | AO | 5069-OF4 | 9 | 0 | VSD-101 | P-101 speed reference | 4-20 mA | Live zero | X4:031/032 | - | SCH-0204
AO-01 | AO | 5069-OF4 | 9 | 1 | VSD-102 | P-102 speed reference | 4-20 mA | Live zero | X4:033/034 | - | SCH-0204
AO-02 | AO | 5069-OF4 | 9 | 2 | - | Spare analogue output | 4-20 mA | Live zero | X4:035 | - | SCH-0204
AO-03 | AO | 5069-OF4 | 9 | 3 | - | Spare analogue output | 4-20 mA | Live zero | X4:037 | - | SCH-0204
RDI-00 | DI (RIO) | 5069-IB16 | RIO-01 | 0 | LDSH-102 | Intake screen differential level high | 24 VDC | NO | RX3:001 | - | RIO-0201
RDI-01 | DI (RIO) | 5069-IB16 | RIO-01 | 1 | SCR-101 | Screen drive running | 24 VDC | NO | RX3:002 | - | RIO-0201
RDI-02 | DI (RIO) | 5069-IB16 | RIO-01 | 2 | SCR-101 | Screen drive fault | 24 VDC | NC | RX3:003 | - | RIO-0201
RDI-03 | DI (RIO) | 5069-IB16 | RIO-01 | 3 | SCR-101 | Screen drive available | 24 VDC | NC | RX3:004 | - | RIO-0201
RDI-04 | DI (RIO) | 5069-IB16 | RIO-01 | 4 | S-SCR-LOR | Screen selector Local | 24 VDC | NO | RX3:005 | - | RIO-0201
RDI-05 | DI (RIO) | 5069-IB16 | RIO-01 | 5 | S-SCR-LOR | Screen selector Remote | 24 VDC | NO | RX3:006 | - | RIO-0201
RDI-06 | DI (RIO) | 5069-IB16 | RIO-01 | 6 | ZSO-102 | Penstock open limit | 24 VDC | NO | RX3:007 | - | RIO-0201
RDI-07 | DI (RIO) | 5069-IB16 | RIO-01 | 7 | ZSC-102 | Penstock closed limit | 24 VDC | NO | RX3:008 | - | RIO-0201
RDI-08 | DI (RIO) | 5069-IB16 | RIO-01 | 8 | RIO-01 | Kiosk door open | 24 VDC | NO | RX3:009 | - | RIO-0201
RDI-09 | DI (RIO) | 5069-IB16 | RIO-01 | 9 | PSU-R1 | Kiosk 24 VDC PSU healthy | 24 VDC | NC | RX3:010 | - | RIO-0201
RDI-10 | DI (RIO) | 5069-IB16 | RIO-01 | 10 | - | Spare digital input | 24 VDC | - | RX3:011 | - | RIO-0201
RDI-11 | DI (RIO) | 5069-IB16 | RIO-01 | 11 | - | Spare digital input | 24 VDC | - | RX3:012 | - | RIO-0201
RDI-12 | DI (RIO) | 5069-IB16 | RIO-01 | 12 | - | Spare digital input | 24 VDC | - | RX3:013 | - | RIO-0201
RDI-13 | DI (RIO) | 5069-IB16 | RIO-01 | 13 | - | Spare digital input | 24 VDC | - | RX3:014 | - | RIO-0201
RDI-14 | DI (RIO) | 5069-IB16 | RIO-01 | 14 | - | Spare digital input | 24 VDC | - | RX3:015 | - | RIO-0201
RDI-15 | DI (RIO) | 5069-IB16 | RIO-01 | 15 | - | Spare digital input | 24 VDC | - | RX3:016 | - | RIO-0201
RAI-00 | AI (RIO) | 5069-IF8 | RIO-01 | 0 | LIT-102 | Screen upstream level (0-4 m) | 4-20 mA | Live zero | RX4:001/002 | - | RIO-0203
RAI-01 | AI (RIO) | 5069-IF8 | RIO-01 | 1 | LIT-103 | Screen downstream level (0-4 m) | 4-20 mA | Live zero | RX4:003/004 | - | RIO-0203
RAI-02 | AI (RIO) | 5069-IF8 | RIO-01 | 2 | - | Spare analogue input | 4-20 mA | Live zero | RX4:005/006 | - | RIO-0203
RAI-03 | AI (RIO) | 5069-IF8 | RIO-01 | 3 | - | Spare analogue input | 4-20 mA | Live zero | RX4:007/008 | - | RIO-0203
RAI-04 | AI (RIO) | 5069-IF8 | RIO-01 | 4 | - | Spare analogue input | 4-20 mA | Live zero | RX4:009/010 | - | RIO-0203
RAI-05 | AI (RIO) | 5069-IF8 | RIO-01 | 5 | - | Spare analogue input | 4-20 mA | Live zero | RX4:011/012 | - | RIO-0203
RAI-06 | AI (RIO) | 5069-IF8 | RIO-01 | 6 | - | Spare analogue input | 4-20 mA | Live zero | RX4:013/014 | - | RIO-0203
RAI-07 | AI (RIO) | 5069-IF8 | RIO-01 | 7 | - | Spare analogue input | 4-20 mA | Live zero | RX4:015/016 | - | RIO-0203

## Cable Schedule
Cable No. | From | To | Service | Type | Cores / Size | Screen | Screen Earthed | Supply Scope | Status
C-0001 | TX-01 LV terminals | MCC-01 X0 | Incoming supply | 415 V power | TBC - client scope | - | - | Client / installer | TBC
C-0101 | MCC-01 VSD-101 output | P-101 motor terminal box | Motor power | VSD motor cable | 3C+E 95 mm2 (provisional) | Screened | BOTH ends, 360 deg EMC gland | Installer | Provisional - pending AS/NZS 3008 calc
C-0102 | MCC-01 X3 | LCS-101 | Pump 1 local control | Control multicore | 16C x 1.5 mm2 | Overall | MCC end only | Installer | IFC
C-0103 | MCC-01 X3 | P-101 motor terminal box | Motor thermistor | Instrument | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0104 | MCC-01 X3 | B101-SEAL seal water flow switch | Seal water proving | Control | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0105 | MCC-01 X5 | LCS-101 E-stop | SAFETY - dual channel | Control | 4C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0111 | MCC-01 VSD-102 output | P-102 motor terminal box | Motor power | VSD motor cable | 3C+E 95 mm2 (provisional) | Screened | BOTH ends, 360 deg EMC gland | Installer | Provisional
C-0112 | MCC-01 X3 | LCS-102 | Pump 2 local control | Control multicore | 16C x 1.5 mm2 | Overall | MCC end only | Installer | IFC
C-0113 | MCC-01 X3 | P-102 motor terminal box | Motor thermistor | Instrument | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0114 | MCC-01 X3 | B102-SEAL seal water flow switch | Seal water proving | Control | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0115 | MCC-01 X5 | LCS-102 E-stop | SAFETY - dual channel | Control | 4C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0121 | MCC-01 X1 | P-103 sump pump | Motor power | Power | 4C x 2.5 mm2 | - | - | Installer | IFC
C-0122 | MCC-01 X3 | Sump float switches LSH/LSL-103 | Level control | Control | 4C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0131 | MCC-01 X1 | C-101 air compressor | Motor power | Power | 4C x 2.5 mm2 | - | - | Installer | IFC
C-0132 | MCC-01 X3 | PSL-101 air pressure switch | Pressure control | Control | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0141 | MCC-01 X1 | MOV-101 actuator | Actuator power | Power | 4C x 2.5 mm2 | - | - | Installer | IFC
C-0142 | MCC-01 X3 | MOV-101 actuator control | Actuator control | Control multicore | 12C x 1.5 mm2 | Overall | MCC end only | Installer | IFC
C-0201 | MCC-01 X4 | LIT-101 wet well level | Level transmitter | Instrument | 1 pr x 1.5 mm2 IS/OS | Individual + overall | MCC end only | Installer | IFC
C-0202 | MCC-01 X4 | FIT-101 discharge flow | Flow transmitter | Instrument | 1 pr x 1.5 mm2 IS/OS | Individual + overall | MCC end only | Installer | IFC
C-0203 | MCC-01 X4 | PIT-101 P-101 discharge pressure | Pressure transmitter | Instrument | 1 pr x 1.5 mm2 IS/OS | Individual + overall | MCC end only | Installer | IFC
C-0204 | MCC-01 X4 | PIT-102 P-102 discharge pressure | Pressure transmitter | Instrument | 1 pr x 1.5 mm2 IS/OS | Individual + overall | MCC end only | Installer | IFC
C-0205 | MCC-01 X4 | PIT-103 common suction pressure | Pressure transmitter | Instrument | 1 pr x 1.5 mm2 IS/OS | Individual + overall | MCC end only | Installer | IFC
C-0206 | MCC-01 X4 | AIT-101 raw water turbidity | Analyser | Instrument | 1 pr x 1.5 mm2 IS/OS | Individual + overall | MCC end only | Installer | IFC
C-0210 | MCC-01 X3 | LSLL-101 low-low float | DRY-RUN TRIP - hardwired | Control | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0211 | MCC-01 X3 | LSHH-101 high-high float | High level alarm | Control | 2C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0301 | MCC-01 X5 | S-ES-PH pump hall E-stop | SAFETY - dual channel | Control | 4C x 1.5 mm2 | Screened | MCC end only | Installer | IFC
C-0401 | MCC-01 X6 | Control room patch panel | SCADA fibre | Fibre optic | 2C OM3 multimode | - | - | Installer | IFC
C-0402 | MCC-01 X6 | RIO-01 intake screen kiosk | Remote I/O fibre | Fibre optic | 2C OM3 multimode | - | - | Installer | IFC
C-0501 | MCC-01 X1 | DB-01 light and power board | Sub-board supply | Power | 4C x 25 mm2 (provisional) | - | - | Installer | Provisional - DB-01 MD by others
C-0502 | MCC-01 X1 | PKG-201 dosing skid isolator | Vendor skid supply | Power | 4C x 6 mm2 (provisional) | - | - | Installer | Provisional - confirm skid FLC
C-0503 | MCC-01 X1 | HVAC-01 switchroom air conditioner | HVAC supply + fault | Power + control | 4C x 4 mm2 + 2C x 1.5 mm2 | - | - | Installer | IFC
C-0601 | DB-01 | RIO-01 intake screen kiosk | Kiosk supply | Power | 4C x 4 mm2 | - | - | Installer | IFC - not our supply

## Termination Schedule
Cable No. | From | To | Core | Terminal | Signal | Voltage | Drawing Reference
C-0001 | TX-01 LV | MCC-01 X0 | L1 | X0:L1 | Incoming active phase 1 | 415 V AC | SLD-0001
C-0001 | TX-01 LV | MCC-01 X0 | L2 | X0:L2 | Incoming active phase 2 | 415 V AC | SLD-0001
C-0001 | TX-01 LV | MCC-01 X0 | L3 | X0:L3 | Incoming active phase 3 | 415 V AC | SLD-0001
C-0001 | TX-01 LV | MCC-01 X0 | N | X0:N | Incoming neutral (full size) | 415 V AC | SLD-0001
C-0001 | TX-01 LV | MCC-01 X0 | E | XE:01 | Incoming protective earth | - | SLD-0001
C-0101 | MCC-01 VSD-101 output | P-101 motor | U | VSD-101 U | Motor phase U | 415 V AC | SCH-0101/02
C-0101 | MCC-01 VSD-101 output | P-101 motor | V | VSD-101 V | Motor phase V | 415 V AC | SCH-0101/02
C-0101 | MCC-01 VSD-101 output | P-101 motor | W | VSD-101 W | Motor phase W | 415 V AC | SCH-0101/02
C-0101 | MCC-01 VSD-101 output | P-101 motor | E | XE:11 | Motor protective earth | - | SCH-0101/02
C-0101 | MCC-01 VSD-101 output | P-101 motor | Screen | EMC gland | 360 deg screen - EARTHED BOTH ENDS | - | SCH-0101/02
C-0111 | MCC-01 VSD-102 output | P-102 motor | U | VSD-102 U | Motor phase U | 415 V AC | SCH-0111/02
C-0111 | MCC-01 VSD-102 output | P-102 motor | V | VSD-102 V | Motor phase V | 415 V AC | SCH-0111/02
C-0111 | MCC-01 VSD-102 output | P-102 motor | W | VSD-102 W | Motor phase W | 415 V AC | SCH-0111/02
C-0111 | MCC-01 VSD-102 output | P-102 motor | E | XE:12 | Motor protective earth | - | SCH-0111/02
C-0111 | MCC-01 VSD-102 output | P-102 motor | Screen | EMC gland | 360 deg screen - EARTHED BOTH ENDS | - | SCH-0111/02
C-0121 | MCC-01 X1 | P-103 sump pump | L1 | X1:001 | Active phase 1 | 415 V AC | SCH-0121/02
C-0121 | MCC-01 X1 | P-103 sump pump | L2 | X1:002 | Active phase 2 | 415 V AC | SCH-0121/02
C-0121 | MCC-01 X1 | P-103 sump pump | L3 | X1:003 | Active phase 3 | 415 V AC | SCH-0121/02
C-0121 | MCC-01 X1 | P-103 sump pump | E | XE:21 | Protective earth | - | SCH-0121/02
C-0131 | MCC-01 X1 | C-101 compressor | L1 | X1:005 | Active phase 1 | 415 V AC | SCH-0131/02
C-0131 | MCC-01 X1 | C-101 compressor | L2 | X1:006 | Active phase 2 | 415 V AC | SCH-0131/02
C-0131 | MCC-01 X1 | C-101 compressor | L3 | X1:007 | Active phase 3 | 415 V AC | SCH-0131/02
C-0131 | MCC-01 X1 | C-101 compressor | E | XE:25 | Protective earth | - | SCH-0131/02
C-0141 | MCC-01 X1 | MOV-101 actuator | L1 | X1:009 | Active phase 1 | 415 V AC | SCH-0141/02
C-0141 | MCC-01 X1 | MOV-101 actuator | L2 | X1:010 | Active phase 2 | 415 V AC | SCH-0141/02
C-0141 | MCC-01 X1 | MOV-101 actuator | L3 | X1:011 | Active phase 3 | 415 V AC | SCH-0141/02
C-0141 | MCC-01 X1 | MOV-101 actuator | E | XE:29 | Protective earth | - | SCH-0141/02
C-0501 | MCC-01 X1 | DB-01 | L1 | X1:013 | Active phase 1 | 415 V AC | SLD-0001
C-0501 | MCC-01 X1 | DB-01 | L2 | X1:014 | Active phase 2 | 415 V AC | SLD-0001
C-0501 | MCC-01 X1 | DB-01 | L3 | X1:015 | Active phase 3 | 415 V AC | SLD-0001
C-0501 | MCC-01 X1 | DB-01 | E | XE:33 | Protective earth | - | SLD-0001
C-0502 | MCC-01 X1 | PKG-201 dosing skid | L1 | X1:017 | Active phase 1 | 415 V AC | SLD-0001
C-0502 | MCC-01 X1 | PKG-201 dosing skid | L2 | X1:018 | Active phase 2 | 415 V AC | SLD-0001
C-0502 | MCC-01 X1 | PKG-201 dosing skid | L3 | X1:019 | Active phase 3 | 415 V AC | SLD-0001
C-0502 | MCC-01 X1 | PKG-201 dosing skid | E | XE:37 | Protective earth | - | SLD-0001
C-0503 | MCC-01 X1 | HVAC-01 | L1 | X1:021 | Active phase 1 | 415 V AC | SLD-0001
C-0503 | MCC-01 X1 | HVAC-01 | L2 | X1:022 | Active phase 2 | 415 V AC | SLD-0001
C-0503 | MCC-01 X1 | HVAC-01 | L3 | X1:023 | Active phase 3 | 415 V AC | SLD-0001
C-0503 | MCC-01 X1 | HVAC-01 | E | XE:41 | Protective earth | - | SLD-0001
C-0102 | LCS-101 | MCC-01 X3 | 1 | X3:001 | LCS Start PB - 24 VDC supply out | 24 V DC | SCH-0101/12
C-0102 | LCS-101 | MCC-01 X3 | 2 | X3:002 | LCS Start PB - return | 24 V DC | SCH-0101/12
C-0102 | LCS-101 | MCC-01 X3 | 3 | X3:003 | LCS Stop PB - 24 VDC supply out | 24 V DC | SCH-0101/13
C-0102 | LCS-101 | MCC-01 X3 | 4 | X3:004 | LCS Stop PB - return (NC, fail-safe) | 24 V DC | SCH-0101/13
C-0102 | LCS-101 | MCC-01 X3 | 5 | X3:005 | LCS selector - Local position | 24 V DC | SCH-0201/04
C-0102 | LCS-101 | MCC-01 X3 | 6 | X3:006 | LCS selector - Remote position | 24 V DC | SCH-0201/05
C-0102 | LCS-101 | MCC-01 X3 | 7 | X3:007 | LCS Running lamp - supply | 24 V DC | SCH-0101/22
C-0102 | LCS-101 | MCC-01 X3 | 8 | X3:008 | LCS Running lamp - return | 24 V DC | SCH-0101/22
C-0102 | LCS-101 | MCC-01 X3 | 9 | X3:009 | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 10 | X3:010 | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 11 | X3:011 | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 12 | X3:012 | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 13 | X3:009a | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 14 | X3:010a | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 15 | X3:011a | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | 16 | X3:012a | SPARE | - | -
C-0102 | LCS-101 | MCC-01 X3 | Screen | XS:01 | Overall screen - MCC END ONLY | - | SCH-0101
C-0103 | P-101 motor TB | MCC-01 X3 | 1 | X3:013 | PTC thermistor leg 1 to KT101 | ELV | SCH-0101/08
C-0103 | P-101 motor TB | MCC-01 X3 | 2 | X3:014 | PTC thermistor leg 2 to KT101 | ELV | SCH-0101/08
C-0103 | P-101 motor TB | MCC-01 X3 | Screen | XS:02 | Screen - MCC END ONLY | - | SCH-0101
C-0104 | B101-SEAL | MCC-01 X3 | 1 | X3:015 | Seal water flow switch - 24 VDC out | 24 V DC | SCH-0201/08
C-0104 | B101-SEAL | MCC-01 X3 | 2 | X3:016 | Seal water flow switch - return (NC) | 24 V DC | SCH-0201/08
C-0104 | B101-SEAL | MCC-01 X3 | Screen | XS:03 | Screen - MCC END ONLY | - | SCH-0201
- | VSD-101 / MCC internal | MCC-01 X3 | - | X3:017 | VSD-101 drive healthy to PLC DI (NC, fail-safe) | 24 V DC | SCH-0201/02
- | VSD-101 / MCC internal | MCC-01 X3 | - | X3:018 | VSD-101 drive running to PLC DI | 24 V DC | SCH-0201/03
- | VSD-101 / MCC internal | MCC-01 X3 | - | X3:019 | KA101 run command to VSD-101 term 18 | 24 V DC | SCH-0101/18
- | VSD-101 / MCC internal | MCC-01 X3 | - | X3:020 | Q11 auxiliary - feeder available to PLC DI | 24 V DC | SCH-0201/01
- | VSD-101 / MCC internal | MCC-01 X3 | - | X3:023 | PLC DO - VSD-101 fault reset | 24 V DC | SCH-0202/02
- | VSD-101 / MCC internal | MCC-01 X3 | - | X3:024 | PLC DO - VSD-101 remote reference enable | 24 V DC | SCH-0202/13
C-0210 | LSLL-101 | MCC-01 X3 | 1 | X3:021 | Low-low float - 24 VDC out | 24 V DC | SCH-0101/09
C-0210 | LSLL-101 | MCC-01 X3 | 2 | X3:022 | Low-low float - return (NC, HARDWIRED DRY-RUN TRIP) | 24 V DC | SCH-0101/09
C-0210 | LSLL-101 | MCC-01 X3 | Screen | XS:04 | Screen - MCC END ONLY | - | SCH-0101
- | - | - | - | X3:025 | SPARE | - | -
- | - | - | - | X3:026 | SPARE | - | -
- | - | - | - | X3:027 | SPARE | - | -
- | - | - | - | X3:028 | SPARE | - | -
- | - | - | - | X3:029 | SPARE | - | -
- | - | - | - | X3:030 | SPARE | - | -
C-0112 | LCS-102 | MCC-01 X3 | 1 | X3:031 | LCS Start PB - 24 VDC supply out | 24 V DC | SCH-0111/12
C-0112 | LCS-102 | MCC-01 X3 | 2 | X3:032 | LCS Start PB - return | 24 V DC | SCH-0111/12
C-0112 | LCS-102 | MCC-01 X3 | 3 | X3:033 | LCS Stop PB - 24 VDC supply out | 24 V DC | SCH-0111/13
C-0112 | LCS-102 | MCC-01 X3 | 4 | X3:034 | LCS Stop PB - return (NC, fail-safe) | 24 V DC | SCH-0111/13
C-0112 | LCS-102 | MCC-01 X3 | 5 | X3:035 | LCS selector - Local position | 24 V DC | SCH-0201/11
C-0112 | LCS-102 | MCC-01 X3 | 6 | X3:036 | LCS selector - Remote position | 24 V DC | SCH-0201/12
C-0112 | LCS-102 | MCC-01 X3 | 7 | X3:037 | LCS Running lamp - supply | 24 V DC | SCH-0111/22
C-0112 | LCS-102 | MCC-01 X3 | 8 | X3:038 | LCS Running lamp - return | 24 V DC | SCH-0111/22
C-0112 | LCS-102 | MCC-01 X3 | 9-16 | X3:039-042 | SPARE (8 cores) | - | -
C-0112 | LCS-102 | MCC-01 X3 | Screen | XS:05 | Overall screen - MCC END ONLY | - | SCH-0111
C-0113 | P-102 motor TB | MCC-01 X3 | 1 | X3:043 | PTC thermistor leg 1 to KT102 | ELV | SCH-0111/08
C-0113 | P-102 motor TB | MCC-01 X3 | 2 | X3:044 | PTC thermistor leg 2 to KT102 | ELV | SCH-0111/08
C-0113 | P-102 motor TB | MCC-01 X3 | Screen | XS:06 | Screen - MCC END ONLY | - | SCH-0111
C-0114 | B102-SEAL | MCC-01 X3 | 1 | X3:045 | Seal water flow switch - 24 VDC out | 24 V DC | SCH-0201/15
C-0114 | B102-SEAL | MCC-01 X3 | 2 | X3:046 | Seal water flow switch - return (NC) | 24 V DC | SCH-0201/15
C-0114 | B102-SEAL | MCC-01 X3 | Screen | XS:07 | Screen - MCC END ONLY | - | SCH-0201
- | VSD-102 / MCC internal | MCC-01 X3 | - | X3:047 | VSD-102 drive healthy to PLC DI (NC, fail-safe) | 24 V DC | SCH-0201/09
- | VSD-102 / MCC internal | MCC-01 X3 | - | X3:048 | VSD-102 drive running to PLC DI | 24 V DC | SCH-0201/10
- | VSD-102 / MCC internal | MCC-01 X3 | - | X3:049 | KA102 run command to VSD-102 term 18 | 24 V DC | SCH-0111/18
- | VSD-102 / MCC internal | MCC-01 X3 | - | X3:050 | Q12 auxiliary - feeder available to PLC DI | 24 V DC | SCH-0201/08
- | VSD-102 / MCC internal | MCC-01 X3 | - | X3:053 | PLC DO - VSD-102 fault reset | 24 V DC | SCH-0202/04
- | VSD-102 / MCC internal | MCC-01 X3 | - | X3:054 | PLC DO - VSD-102 remote reference enable | 24 V DC | SCH-0202/14
- | - | - | - | X3:055 | SPARE | - | -
- | - | - | - | X3:056 | SPARE | - | -
- | - | - | - | X3:057 | SPARE | - | -
- | - | - | - | X3:058 | SPARE | - | -
- | - | - | - | X3:059 | SPARE | - | -
- | - | - | - | X3:060 | SPARE | - | -
- | MCC internal | MCC-01 X3 | - | X3:061 | Q15 MPCB auxiliary - P-103 feeder available | 24 V DC | SCH-0201/16
- | MCC internal | MCC-01 X3 | - | X3:062 | KM103 auxiliary - P-103 running | 24 V DC | SCH-0201/17
- | MCC internal | MCC-01 X3 | - | X3:063 | S103-LOR Local position | 24 V DC | SCH-0201/18
- | MCC internal | MCC-01 X3 | - | X3:064 | S103-LOR Remote position | 24 V DC | SCH-0201/19
- | MCC internal | MCC-01 X3 | - | X3:067 | PLC DO - KM103 start command | 24 V DC | SCH-0202/05
C-0122 | Sump floats | MCC-01 X3 | 1 | X3:065 | LSH-103 sump high level float - start | 24 V DC | SCH-0201/20
C-0122 | Sump floats | MCC-01 X3 | 2 | X3:065r | LSH-103 return | 24 V DC | SCH-0201/20
C-0122 | Sump floats | MCC-01 X3 | 3 | X3:066 | LSL-103 sump low level float - stop (NC) | 24 V DC | SCH-0201/21
C-0122 | Sump floats | MCC-01 X3 | 4 | X3:066r | LSL-103 return | 24 V DC | SCH-0201/21
C-0122 | Sump floats | MCC-01 X3 | Screen | XS:08 | Screen - MCC END ONLY | - | SCH-0201
- | MCC internal | MCC-01 X3 | - | X3:071 | Q16 MPCB auxiliary - C-101 feeder available | 24 V DC | SCH-0201/22
- | MCC internal | MCC-01 X3 | - | X3:072 | KM101C auxiliary - C-101 running | 24 V DC | SCH-0201/23
- | MCC internal | MCC-01 X3 | - | X3:074 | PLC DO - KM101C start command | 24 V DC | SCH-0202/06
C-0132 | PSL-101 | MCC-01 X3 | 1 | X3:073 | Instrument air pressure low switch | 24 V DC | SCH-0201/24
C-0132 | PSL-101 | MCC-01 X3 | 2 | X3:073r | Return | 24 V DC | SCH-0201/24
C-0132 | PSL-101 | MCC-01 X3 | Screen | XS:09 | Screen - MCC END ONLY | - | SCH-0201
C-0142 | MOV-101 actuator | MCC-01 X3 | 1 | X3:081 | ZSO-101 valve opened limit | 24 V DC | SCH-0201/25
C-0142 | MOV-101 actuator | MCC-01 X3 | 2 | X3:082 | ZSC-101 valve closed limit | 24 V DC | SCH-0201/26
C-0142 | MOV-101 actuator | MCC-01 X3 | 3 | X3:083 | Actuator fault (NC, vendor contact) | 24 V DC | SCH-0201/27
C-0142 | MOV-101 actuator | MCC-01 X3 | 4 | X3:084 | Actuator remote selected (vendor contact) | 24 V DC | SCH-0201/28
C-0142 | MOV-101 actuator | MCC-01 X3 | 5 | X3:085 | PLC DO - open command | 24 V DC | SCH-0202/07
C-0142 | MOV-101 actuator | MCC-01 X3 | 6 | X3:086 | PLC DO - close command | 24 V DC | SCH-0202/08
C-0142 | MOV-101 actuator | MCC-01 X3 | 7 | X3:087 | PLC DO - stop command | 24 V DC | SCH-0202/09
C-0142 | MOV-101 actuator | MCC-01 X3 | 8 | X3:088 | Common return | 24 V DC | SCH-0141
C-0142 | MOV-101 actuator | MCC-01 X3 | 9-12 | X3:089-090 | SPARE (4 cores) | - | -
C-0142 | MOV-101 actuator | MCC-01 X3 | Screen | XS:10 | Overall screen - MCC END ONLY | - | SCH-0141
C-0503 | HVAC-01 | MCC-01 X3 | C1 | X3:091 | HVAC fault (NC) - drives ramp to min speed | 24 V DC | SCH-0201/29
C-0503 | HVAC-01 | MCC-01 X3 | C2 | X3:091r | Return | 24 V DC | SCH-0201/29
- | - | - | - | X3:092 | SPARE | - | -
- | - | - | - | X3:093 | SPARE | - | -
- | MCC internal | MCC-01 X3 | - | X3:101 | KS-01 safety relay auxiliary - E-stop circuit healthy | 24 V DC | SCH-0202/01
- | MCC internal | MCC-01 X3 | - | X3:102 | Q1 OF auxiliary - incomer closed | 24 V DC | SCH-0202/02
- | MCC internal | MCC-01 X3 | - | X3:103 | Q1 SD auxiliary - incomer tripped | 24 V DC | SCH-0202/03
- | MCC internal | MCC-01 X3 | - | X3:104 | KVP-01 phase failure relay healthy (NC) | 24 V DC | SCH-0202/04
- | MCC internal | MCC-01 X3 | - | X3:105 | SPD-01 surge diverter status (NC) | 24 V DC | SCH-0202/05
- | MCC internal | MCC-01 X3 | - | X3:106 | PSU-1 healthy (NC) | 24 V DC | SCH-0202/06
- | MCC internal | MCC-01 X3 | - | X3:107 | PSU-2 healthy (NC) | 24 V DC | SCH-0202/07
- | MCC internal | MCC-01 X3 | - | X3:108 | UPS-01 on battery | 24 V DC | SCH-0202/08
- | MCC internal | MCC-01 X3 | - | X3:109 | UPS-01 fault | 24 V DC | SCH-0202/09
- | MCC internal | MCC-01 X3 | - | X3:110 | ECP group trip common (NC) | 24 V DC | SCH-0202/10
- | MCC internal | MCC-01 X3 | - | X3:121 | PLC DO - common alarm beacon | 24 V DC | SCH-0202/10
- | MCC internal | MCC-01 X3 | - | X3:122 | PLC DO - common alarm sounder | 24 V DC | SCH-0202/11
- | MCC internal | MCC-01 X3 | - | X3:123 | PLC DO - station healthy watchdog to SCADA | 24 V DC | SCH-0202/12
C-0211 | LSHH-101 | MCC-01 X3 | 1 | X3:111 | Wet well high-high float (NC) | 24 V DC | SCH-0202/11
C-0211 | LSHH-101 | MCC-01 X3 | 2 | X3:111r | Return | 24 V DC | SCH-0202/11
C-0211 | LSHH-101 | MCC-01 X3 | Screen | XS:11 | Screen - MCC END ONLY | - | SCH-0202
- | - | - | - | X3:112 | SPARE | - | -
- | - | - | - | X3:113 | SPARE | - | -
- | - | - | - | X3:114 | SPARE | - | -
- | - | - | - | X3:115 | SPARE | - | -
C-0201 | LIT-101 wet well level | MCC-01 X4 | + | X4:001 | LIT-101 wet well level 4-20 mA loop + (DISCONNECT TERMINAL) | 24 V DC loop | SCH-0203/01
C-0201 | LIT-101 wet well level | MCC-01 X4 | - | X4:002 | LIT-101 wet well level 4-20 mA loop - | 24 V DC loop | SCH-0203/01
C-0201 | LIT-101 wet well level | MCC-01 X4 | Screen | XS:20 | Screen - MCC END ONLY | - | SCH-0203/01
C-0202 | FIT-101 discharge flow | MCC-01 X4 | + | X4:003 | FIT-101 discharge flow 4-20 mA loop + (DISCONNECT TERMINAL) | 24 V DC loop | SCH-0203/02
C-0202 | FIT-101 discharge flow | MCC-01 X4 | - | X4:004 | FIT-101 discharge flow 4-20 mA loop - | 24 V DC loop | SCH-0203/02
C-0202 | FIT-101 discharge flow | MCC-01 X4 | Screen | XS:21 | Screen - MCC END ONLY | - | SCH-0203/02
C-0203 | PIT-101 P-101 discharge pressure | MCC-01 X4 | + | X4:005 | PIT-101 P-101 discharge pressure 4-20 mA loop + (DISCONNECT TERMINAL) | 24 V DC loop | SCH-0203/03
C-0203 | PIT-101 P-101 discharge pressure | MCC-01 X4 | - | X4:006 | PIT-101 P-101 discharge pressure 4-20 mA loop - | 24 V DC loop | SCH-0203/03
C-0203 | PIT-101 P-101 discharge pressure | MCC-01 X4 | Screen | XS:22 | Screen - MCC END ONLY | - | SCH-0203/03
C-0204 | PIT-102 P-102 discharge pressure | MCC-01 X4 | + | X4:007 | PIT-102 P-102 discharge pressure 4-20 mA loop + (DISCONNECT TERMINAL) | 24 V DC loop | SCH-0203/04
C-0204 | PIT-102 P-102 discharge pressure | MCC-01 X4 | - | X4:008 | PIT-102 P-102 discharge pressure 4-20 mA loop - | 24 V DC loop | SCH-0203/04
C-0204 | PIT-102 P-102 discharge pressure | MCC-01 X4 | Screen | XS:23 | Screen - MCC END ONLY | - | SCH-0203/04
C-0205 | PIT-103 common suction pressure | MCC-01 X4 | + | X4:009 | PIT-103 common suction pressure 4-20 mA loop + (DISCONNECT TERMINAL) | 24 V DC loop | SCH-0203/05
C-0205 | PIT-103 common suction pressure | MCC-01 X4 | - | X4:010 | PIT-103 common suction pressure 4-20 mA loop - | 24 V DC loop | SCH-0203/05
C-0205 | PIT-103 common suction pressure | MCC-01 X4 | Screen | XS:24 | Screen - MCC END ONLY | - | SCH-0203/05
C-0206 | AIT-101 raw water turbidity | MCC-01 X4 | + | X4:011 | AIT-101 raw water turbidity 4-20 mA loop + (DISCONNECT TERMINAL) | 24 V DC loop | SCH-0203/06
C-0206 | AIT-101 raw water turbidity | MCC-01 X4 | - | X4:012 | AIT-101 raw water turbidity 4-20 mA loop - | 24 V DC loop | SCH-0203/06
C-0206 | AIT-101 raw water turbidity | MCC-01 X4 | Screen | XS:25 | Screen - MCC END ONLY | - | SCH-0203/06
- | - | - | - | X4:013 | SPARE - disconnect type | - | -
- | - | - | - | X4:014 | SPARE - disconnect type | - | -
- | - | - | - | X4:015 | SPARE - disconnect type | - | -
- | - | - | - | X4:016 | SPARE - disconnect type | - | -
- | - | - | - | X4:017 | SPARE - disconnect type | - | -
- | - | - | - | X4:018 | SPARE - disconnect type | - | -
- | - | - | - | X4:019 | SPARE - disconnect type | - | -
- | - | - | - | X4:020 | SPARE - disconnect type | - | -
- | - | - | - | X4:021 | SPARE - disconnect type | - | -
- | - | - | - | X4:022 | SPARE - disconnect type | - | -
- | - | - | - | X4:023 | SPARE - disconnect type | - | -
- | - | - | - | X4:024 | SPARE - disconnect type | - | -
- | - | - | - | X4:025 | SPARE - disconnect type | - | -
- | - | - | - | X4:026 | SPARE - disconnect type | - | -
- | - | - | - | X4:027 | SPARE - disconnect type | - | -
- | - | - | - | X4:028 | SPARE - disconnect type | - | -
- | - | - | - | X4:029 | SPARE - disconnect type | - | -
- | - | - | - | X4:030 | SPARE - disconnect type | - | -
- | PLC AO ch.0 | VSD-101 term 53/55 | - | X4:031 | P-101 speed reference 4-20 mA + (DISCONNECT) | - | SCH-0204/01
- | PLC AO ch.0 | VSD-101 term 53/55 | - | X4:032 | P-101 speed reference 4-20 mA - | - | SCH-0204/01
- | PLC AO ch.1 | VSD-102 term 53/55 | - | X4:033 | P-102 speed reference 4-20 mA + (DISCONNECT) | - | SCH-0204/02
- | PLC AO ch.1 | VSD-102 term 53/55 | - | X4:034 | P-102 speed reference 4-20 mA - | - | SCH-0204/02
- | - | - | - | X4:035 | SPARE - disconnect type | - | -
- | - | - | - | X4:036 | SPARE - disconnect type | - | -
- | - | - | - | X4:037 | SPARE - disconnect type | - | -
- | - | - | - | X4:038 | SPARE - disconnect type | - | -
- | S-ES-MCC (MCC door) | MCC-01 X5 | - | X5:001 | E-stop MCC door, channel A in (YELLOW) | 24 V DC | SCH-0040/02
- | S-ES-MCC (MCC door) | MCC-01 X5 | - | X5:002 | E-stop MCC door, channel A out (YELLOW) | 24 V DC | SCH-0040/02
- | S-ES-MCC (MCC door) | MCC-01 X5 | - | X5:003 | E-stop MCC door, channel B in (YELLOW) | 24 V DC | SCH-0040/02
- | S-ES-MCC (MCC door) | MCC-01 X5 | - | X5:004 | E-stop MCC door, channel B out (YELLOW) | 24 V DC | SCH-0040/02
C-0105 | LCS-101 E-stop | MCC-01 X5 | 1 | X5:005 | E-stop 101, channel A in (YELLOW) | 24 V DC | SCH-0040/03
C-0105 | LCS-101 E-stop | MCC-01 X5 | 2 | X5:006 | E-stop 101, channel A out (YELLOW) | 24 V DC | SCH-0040/03
C-0105 | LCS-101 E-stop | MCC-01 X5 | 3 | X5:007 | E-stop 101, channel B in (YELLOW) | 24 V DC | SCH-0040/04
C-0105 | LCS-101 E-stop | MCC-01 X5 | 4 | X5:008 | E-stop 101, channel B out (YELLOW) | 24 V DC | SCH-0040/04
C-0105 | LCS-101 E-stop | MCC-01 X5 | Screen | XS:30 | Screen - MCC END ONLY | - | SCH-0040
C-0115 | LCS-102 E-stop | MCC-01 X5 | 1 | X5:009 | E-stop 102, channel A in (YELLOW) | 24 V DC | SCH-0040/05
C-0115 | LCS-102 E-stop | MCC-01 X5 | 2 | X5:010 | E-stop 102, channel A out (YELLOW) | 24 V DC | SCH-0040/05
C-0115 | LCS-102 E-stop | MCC-01 X5 | 3 | X5:011 | E-stop 102, channel B in (YELLOW) | 24 V DC | SCH-0040/06
C-0115 | LCS-102 E-stop | MCC-01 X5 | 4 | X5:012 | E-stop 102, channel B out (YELLOW) | 24 V DC | SCH-0040/06
C-0115 | LCS-102 E-stop | MCC-01 X5 | Screen | XS:31 | Screen - MCC END ONLY | - | SCH-0040
C-0301 | S-ES-PH pump hall E-stop | MCC-01 X5 | 1 | X5:013 | E-stop pump hall, channel A in (YELLOW) | 24 V DC | SCH-0040/07
C-0301 | S-ES-PH pump hall E-stop | MCC-01 X5 | 2 | X5:014 | E-stop pump hall, channel A out (YELLOW) | 24 V DC | SCH-0040/07
C-0301 | S-ES-PH pump hall E-stop | MCC-01 X5 | 3 | X5:015 | E-stop pump hall, channel B in (YELLOW) | 24 V DC | SCH-0040/08
C-0301 | S-ES-PH pump hall E-stop | MCC-01 X5 | 4 | X5:016 | E-stop pump hall, channel B out (YELLOW) | 24 V DC | SCH-0040/08
C-0301 | S-ES-PH pump hall E-stop | MCC-01 X5 | Screen | XS:32 | Screen - MCC END ONLY | - | SCH-0040
- | KS-01 safety relay | VSD STO | - | X5:017 | KS-01 output 13/14 to VSD-101 STO ch.1 (term 37) | 24 V DC | SCH-0040/12
- | KS-01 safety relay | VSD STO | - | X5:018 | KS-01 output 23/24 to VSD-101 STO ch.2 (term 38) | 24 V DC | SCH-0040/12
- | KS-01 safety relay | VSD STO | - | X5:019 | KS-01 output 13/14 to VSD-102 STO ch.1 (term 37) | 24 V DC | SCH-0040/13
- | KS-01 safety relay | VSD STO | - | X5:020 | KS-01 output 23/24 to VSD-102 STO ch.2 (term 38) | 24 V DC | SCH-0040/13
- | - | - | - | X5:021 | SPARE (YELLOW) - reserved for future E-stop, loop in series | - | SCH-0040 note 3
- | - | - | - | X5:022 | SPARE (YELLOW) - reserved for future E-stop, loop in series | - | SCH-0040 note 3
- | - | - | - | X5:023 | SPARE (YELLOW) - reserved for future E-stop, loop in series | - | SCH-0040 note 3
- | - | - | - | X5:024 | SPARE (YELLOW) - reserved for future E-stop, loop in series | - | SCH-0040 note 3
C-0401 | MCC-01 X6 | Control room patch panel | Fibre 1 | X6-LIU:01 | OM3 multimode Tx to control room | - | SCH-0301/01
C-0401 | MCC-01 X6 | Control room patch panel | Fibre 2 | X6-LIU:02 | OM3 multimode Rx from control room | - | SCH-0301/01
C-0402 | MCC-01 X6 | RIO-01 intake kiosk | Fibre 1 | X6-LIU:03 | OM3 multimode Tx to RIO-01 | - | SCH-0301/02
C-0402 | MCC-01 X6 | RIO-01 intake kiosk | Fibre 2 | X6-LIU:04 | OM3 multimode Rx from RIO-01 | - | SCH-0301/02
- | SW-01 managed switch | MCC internal | - | X6-RJ:01 | PLC 5069-L306ER port A1 | - | SCH-0301/03
- | SW-01 managed switch | MCC internal | - | X6-RJ:02 | VSD-101 EtherNet/IP | - | SCH-0301/04
- | SW-01 managed switch | MCC internal | - | X6-RJ:03 | VSD-102 EtherNet/IP | - | SCH-0301/05
- | SW-01 managed switch | MCC internal | - | X6-RJ:04 | PM-01 power meter | - | SCH-0301/06
- | SW-01 managed switch | MCC internal | - | X6-RJ:05 | Service / laptop port (bulkhead) | - | SCH-0301/07
- | SW-01 managed switch | MCC internal | - | X6-RJ:06 | SPARE | - | -

## BOM
Item | Category | Description | Manufacturer | Part Number | Qty | Rating | Drawing Reference | Lead Time | Status | Notes
A01 | Enclosure | MCC enclosure, floor standing, Form 3b, 5 cubicles, 2300H x 3000W x 600D | Panel builder (custom) | Per NFD-ELE-GA-0020 | 1 | IP42 indoor | GA-0020 | 8 wks fab | HOLD | Cable entry direction blocked release (TQ-001). AS/NZS 61439.1 design verification evidence required for MDR. Rev 1: drive cubicles enlarged - CR-001
A02 | Enclosure | Gland plate, removable, undrilled, aluminium, 600 x 400 | Panel builder | Per GA-0020 | 5 | - | GA-0020 | With A01 | HOLD | Non-magnetic. Bonded to cubicle earth. UNDRILLED - saved rework at CR-001
A03 | Enclosure | Plinth, 100 mm, galvanised | Panel builder | Per GA-0020 | 1 set | - | GA-0020 | With A01 | HOLD | Confirm against civil plinth
A04 | Enclosure | Cubicle internal lighting, LED, with door switch | Rittal | SZ 2500.100 | 5 | 240 V AC | SCH-0030/22 | 3 wks | OK
A05 | Enclosure | GPO, double, 10 A, DIN mount | Clipsal | 56 series equiv. DIN | 2 | 240 V AC | SCH-0030/24 | 2 wks | OK | For laptop at FAT and site
A06 | Enclosure | Anti-condensation heater, 50 W, with guard | Rittal | SK 3105.340 | 5 | 240 V AC | SCH-0030/26 | 3 wks | OK | Heat source - include in thermal declaration
A07 | Enclosure | Hygrostat, DIN mount | Rittal | SK 3118.000 | 2 | - | SCH-0030/26 | 3 wks | OK
A08 | Enclosure | Door earth bonding strap, flexible, 4 mm2, 300 mm | Generic | - | 12 | - | GA-0020 | 1 wk | OK | Every door carrying equipment - hinges are not an earth path
A09 | Enclosure | Main earth bar, tinned copper, 50 x 6, full board length | Panel builder | - | 1 | - | SLD-0001 | With A01 | HOLD
A10 | Enclosure | Instrument screen earth bar, insulated, 25 x 3 | Panel builder | - | 1 | - | TRM-0401 | With A01 | HOLD | SINGLE-POINT bonded to A09 - see FD-003
A11 | Enclosure | Busbar system, 800 A, 3P + full N, supports and shrouding | Panel builder | Per GA-0020 | 1 set | 800 A, Icw TBC | SLD-0001 | With A01 | HOLD | Icw cannot be finalised until fault level confirmed (TQ-002). FULL-SIZE neutral for triplen harmonics
A12 | Enclosure | Escutcheon / blanking panels for spare chassis space | Panel builder | - | 1 set | - | GA-0020 | With A01 | HOLD
B01 | Incomer | Main circuit breaker, MCCB, 4-pole, electronic trip unit | Schneider Electric | ComPacT NSX630N + MicroLogic 2.3 | 1 | 630 A, Icu 50 kA @ 415 V | SLD-0001 | 8-10 wks | HOLD | Icu provisional against 25 kA assumption (TQ-002). Settings from coordination study - not available
B02 | Incomer | Rotary handle, door-interlocked, lockable off, extended | Schneider Electric | ComPacT rotary handle kit | 1 | - | GA-0020 | With B01 | HOLD
B03 | Incomer | Auxiliary contact kit - OF (status) + SD (trip indication) | Schneider Electric | ComPacT aux kit | 1 set | - | SCH-0202/02 | With B01 | HOLD | Status and trip are DIFFERENT alarms
B04 | Incomer | Current transformer, 600/5 A, metering class | Schneider Electric | METSECT5MB060 | 3 | 600/5, Cl. 0.5 | SLD-0001 | 6 wks | TBC | Class and burden to be verified against meter + lead length. Confirm if revenue-grade metering required
B05 | Incomer | Power meter, EtherNet/IP | Schneider Electric | PowerLogic PM5560 (METSEPM5560) | 1 | - | SLD-0001 | 6 wks | OK | Energy, PQ logging, harmonic indication
B06 | Incomer | Surge protective device, Type 1+2 | Schneider Electric | Acti9 iPRD1 25r | 1 | 3P+N | SLD-0001 | 4 wks | OK | Status contact to PLC. Connecting lead length critical to performance
B07 | Incomer | SPD protective device, 3P+N | Schneider Electric | Acti9 iC60 (rating per SPD manual) | 1 | Per B06 manual | SLD-0001 | 4 wks | TBC | Rating MUST come from SPD manual, not guessed
B08 | Incomer | Phase failure / phase sequence relay | Schneider Electric | Zelio RM35TF30 | 1 | 415 V | SCH-0202/04 | 4 wks | OK | Permissive + alarm, not a trip
C01 | VSD feeder | Feeder MCCB, 3-pole | Schneider Electric | ComPacT NSX250N, TMD trip | 2 | 250 A, Icu 50 kA | SLD-0001 | 8 wks | HOLD | Rating MUST be confirmed from drive manual, not motor FLC. Rev 1: frame unchanged after CR-001, setting revised
C02 | VSD feeder | Rotary handle, door-interlocked, lockable | Schneider Electric | ComPacT handle kit | 2 | - | GA-0020 | With C01 | HOLD
C03 | VSD feeder | Auxiliary contacts, OF + SD | Schneider Electric | ComPacT aux kit | 2 set | - | SCH-0201/01 | With C01 | HOLD
C04 | VSD feeder | Variable speed drive, 90 kW, 380-480 V | Danfoss | VLT AQUA Drive FC202, type code TBC | 2 | 90 kW, 415 V | SLD-0001, SCH-0101 | 14-16 wks | HOLD | LONGEST LEAD ITEM. Rev D: 75 kW to 90 kW per CR-001. Order had NOT been placed - no cancellation cost. Type code must be finalised before PO. See DR-005
C05 | VSD feeder | Line reactor, 3% impedance | Danfoss | Per drive selection guide | 2 | 90 kW | SLD-0001 | 10 wks | HOLD | Provisional - subject to harmonic assessment TQ-006 and confirmed motor cable length. May be superseded by active harmonic filter
C06 | VSD feeder | EMC cable gland, 360 deg screen termination | CMP / Lapp | Size to suit final cable | 4 | - | TRM-0401 | 4 wks | TBC | Held pending cable size - saved wrong stock at CR-001
C07 | VSD feeder | PTC thermistor protection relay | Schneider Electric | TeSys LT3SA00M | 2 | 24 V DC | SCH-0101/08 | 6 wks | TBC | Independent of drive thermal model. See FD-001
C08 | VSD feeder | Interposing relay, run command | Phoenix Contact | PLC-RSC-24DC/21 | 2 | 24 V DC, 6 A | SCH-0101/18 | 2 wks | OK
D01 | DOL feeder | Motor protection circuit breaker, P-103 | Schneider Electric | TeSys GV2ME14 | 1 | 6-10 A | SLD-0001 | 4 wks | OK | Set to confirmed motor FLC
D02 | DOL feeder | Motor protection circuit breaker, C-101 | Schneider Electric | TeSys GV2ME16 | 1 | 9-14 A | SLD-0001 | 4 wks | OK
D03 | DOL feeder | Motor protection circuit breaker, MOV-101 | Schneider Electric | TeSys GV2ME08 | 1 | 2.5-4 A | SLD-0001 | 4 wks | OK
D04 | DOL feeder | Contactor, AC-3, 24 V DC coil | Schneider Electric | TeSys LC1D09BD | 2 | 9 A AC-3 | SCH-0121 | 4 wks | TBC | AC-3 rating NOT AC-1. Type 2 coordination with D01/D02 verified against manufacturer tables. See FD-002 (240 V AC coil supplied in error)
D05 | DOL feeder | Auxiliary contact block, 1 NO + 1 NC | Schneider Electric | LADN11 | 2 | - | SCH-0121 | 4 wks | OK
D05a | DOL feeder | Auxiliary contact block, 2 NO (ADDED - DR-002) | Schneider Electric | LADN20 | 2 | - | SCH-0121/14 | 4 wks | OK | ADDED at Rev C - schematic uses 4 contacts, base device supplies 2. See DR-002
D06 | Distribution | MCCB, 3-pole, DB-01 feeder | Schneider Electric | ComPacT NSX100N TMD80 | 1 | 80 A | SLD-0001 | 8 wks | OK | DB-01 maximum demand is DB-01 designer's responsibility
D07 | Distribution | MCCB, 3-pole, PKG-201 feeder | Schneider Electric | ComPacT NSX100N TMD32 | 1 | 32 A | SLD-0001 | 8 wks | TBC | Confirm skid declared FLC from FINAL vendor data sheet
D08 | Distribution | MCB, 3-pole, C-curve, HVAC-01 | Schneider Electric | Acti9 iC60N 3P C20 | 1 | 20 A | SLD-0001 | 2 wks | OK
D09 | Distribution | MCCB, 3-pole, SPARE FEEDER 1 | Schneider Electric | ComPacT NSX100N TMD63 | 1 | 63 A | SLD-0001 | 8 wks | OK | Fitted AND wired to terminals - adding later costs a shutdown
D10 | Distribution | MCCB, 3-pole, SPARE FEEDER 2 | Schneider Electric | ComPacT NSX100N TMD32 | 1 | 32 A | SLD-0001 | 8 wks | OK | Fitted AND wired to terminals
E01 | Control power | UPS, online, with volt-free status contacts | Eaton | 9SX 1000i (or equivalent) | 1 | 1 kVA | SCH-0030/02 | 10 wks | TBC | Autonomy to be confirmed against actual control load. Confirm status contacts are included, not an option
E02 | Control power | Power supply, 24 V DC, 20 A, switch-mode | Phoenix Contact | QUINT4-PS/1AC/24DC/20 | 2 | 24 V DC 20 A | SCH-0030/06 | 6 wks | OK | EACH sized for FULL load, not half
E03 | Control power | Redundancy (O-ring) module | Phoenix Contact | QUINT4-ORING/24DC/2X20/1X40 | 1 | 40 A | SCH-0030/08 | 6 wks | OK | Not a direct parallel connection
E04 | Control power | Electronic circuit protector, DC, adjustable, with status | Phoenix Contact | CBM E4 24DC series | 6 | 24 V DC | SCH-0030/10-20 | 6 wks | OK | DC-RATED. AC MCBs are not acceptable on DC - no natural current zero
E05 | Control power | MCB, 1-pole, C-curve, 10 A | Schneider Electric | Acti9 iC60N 1P C10 | 2 | 10 A | SCH-0030/04 | 2 wks | OK | Separate MCB per PSU - single trip cannot take out both
E06 | Control power | MCB, 1-pole, C-curve, 16 A | Schneider Electric | Acti9 iC60N 1P C16 | 1 | 16 A | SCH-0030/22 | 2 wks | OK | Cubicle services
E07 | Control power | 24 V DC distribution terminal block, feed-through | Phoenix Contact | PTFIX series | 4 | 24 V DC | SCH-0030/09 | 2 wks | OK
F01 | Safety | Safety relay, dual channel, monitored manual reset | Pilz | PNOZ s4 | 1 | 24 V DC | SCH-0040 | 8 wks | HOLD | Selection PROVISIONAL - required Performance Level not determined (TQ-003). May change if PLe required
F02 | Safety | Emergency stop, 40 mm mushroom, twist release, 2 x NC | Schneider Electric | Harmony XB5AS8445 | 1 | 24 V DC | SCH-0040/02 | 3 wks | OK | MCC door
F03 | Safety | Emergency stop, IP66, 2 x NC (for LCS) | Schneider Electric | Harmony XB5AS8445 + IP66 mounting | 2 | 24 V DC | SCH-0040/03-06 | 3 wks | OK | In LCS-101 / LCS-102
F04 | Safety | Emergency stop, IP66 enclosed field station, 2 x NC | Schneider Electric | Harmony XALK178 | 1 | 24 V DC | SCH-0040/07 | 4 wks | OK | Pump hall entry
F05 | Safety | Reset pushbutton, blue, illuminated | Schneider Electric | Harmony XB5AW36B5 | 1 | 24 V DC | SCH-0040/10 | 3 wks | OK | Monitored reset - acts on RELEASE, not press
G01 | PLC | Controller, CompactLogix 5380 | Rockwell Automation | 5069-L306ER | 1 | - | SCH-0201 | 10-12 wks | OK | Platform confirmed TQ-007 Wk9
G02 | PLC | Digital input module, 16 pt, 24 V DC sinking | Rockwell Automation | 5069-IB16 | 3 | 24 V DC | SCH-0201/02 | 10 wks | OK | 40 points used, 8 spare (20%)
G03 | PLC | Digital output module, 16 pt, 24 V DC sourcing | Rockwell Automation | 5069-OB16 | 2 | 24 V DC | SCH-0202 | 10 wks | OK | 14 used, 18 spare - module granularity
G04 | PLC | Analogue input module, 8 ch, current/voltage | Rockwell Automation | 5069-IF8 | 2 | 4-20 mA | SCH-0203 | 10 wks | OK | 6 used, 10 spare
G05 | PLC | Analogue output module, 4 ch | Rockwell Automation | 5069-OF4 | 1 | 4-20 mA | SCH-0204 | 10 wks | OK | 2 used, 2 spare
G06 | PLC | Field potential distributor | Rockwell Automation | 5069-FPD | 2 | - | SCH-0201 | 10 wks | OK | Segments field power between module groups
G07 | PLC | Address reserve module (spare slot placeholder) | Rockwell Automation | 5069-ARM | 1 | - | SCH-0201 | 10 wks | OK | Keeps a slot addressable for future expansion
G08 | PLC | SD card, industrial | Rockwell Automation | 1784-SD2 | 2 | - | - | 4 wks | OK | One installed, one spare for the client
G09 | PLC | End cap, DIN rail, mounting accessories | Rockwell Automation | 5069-ECR + accessories | 1 set | - | SCH-0201 | 10 wks | OK | COMMONLY FORGOTTEN - the chassis does not work without the end cap
G10 | PLC | EtherNet/IP adapter for RIO-01 | Rockwell Automation | 5069-AEN2TR | 1 | - | RIO-0201 | 10 wks | OK | Dual-port for future ring topology
G11 | PLC | Digital input module for RIO-01 | Rockwell Automation | 5069-IB16 | 1 | 24 V DC | RIO-0201 | 10 wks | OK | 10 used, 6 spare
G12 | PLC | Analogue input module for RIO-01 | Rockwell Automation | 5069-IF8 | 1 | 4-20 mA | RIO-0203 | 10 wks | OK | 2 used, 6 spare
H01 | Network | Managed Ethernet switch, 8 port, multimode fibre | Moxa | EDS-408A-MM-SC | 1 | 24 V DC | SCH-0301 | 8 wks | TBC | DR-004: only 2 fibre ports = zero spare. 4-port variant recommended to client. Fed from ECP1 (PLC/network group) NOT field I/O group
H02 | Network | Fibre optic termination enclosure / LIU, DIN mount | Generic | - | 1 | - | SCH-0301 | 4 wks | OK
H03 | Network | Fibre pigtails, OM3, SC, 1 m | Generic | - | 8 | - | SCH-0301 | 4 wks | OK
H04 | Network | Patch lead, Cat6 industrial, 1 m | Generic | - | 8 | - | SCH-0301 | 2 wks | OK | PLC, drives, meter, spare
H05 | Network | RJ45 bulkhead patch panel, DIN | Generic | - | 1 | - | SCH-0301 | 2 wks | OK | Service port on X6
I01 | Indication | Selector switch, 3-position stay-put, Local/Off/Remote | Schneider Electric | Harmony XB5AD33 | 3 | 24 V DC | SCH-0101/02 | 3 wks | OK | P-101, P-102, P-103
I02 | Indication | Pushbutton, flush, green, Start | Schneider Electric | Harmony XB5AA31 | 4 | 24 V DC | SCH-0101/12 | 3 wks | OK
I03 | Indication | Pushbutton, flush, red, Stop | Schneider Electric | Harmony XB5AA42 | 4 | 24 V DC | SCH-0101/13 | 3 wks | OK
I04 | Indication | Pilot light, LED, green - Running | Schneider Electric | Harmony XB5AVB3 | 6 | 24 V DC | SCH-0101/22 | 3 wks | OK | Qty corrected 4 to 6 at Rev C - see DR-001
I05 | Indication | Pilot light, LED, red - Fault | Schneider Electric | Harmony XB5AVB4 | 6 | 24 V DC | SCH-0101/23 | 3 wks | OK
I06 | Indication | Pilot light, LED, white - Available | Schneider Electric | Harmony XB5AVB1 | 6 | 24 V DC | SCH-0101/21 | 3 wks | OK
I07 | Indication | Pushbutton, flush, blue - Lamp test | Schneider Electric | Harmony XB5AA61 | 1 | 24 V DC | SCH-0030/30 | 3 wks | OK | Without lamp test, a failed lamp reads as NOT RUNNING
I08 | Indication | Beacon and sounder, common alarm | Auer / Werma | 24 V DC combination unit | 1 | 24 V DC | SCH-0202/10 | 4 wks | TBC | Confirm client requires local audible alarm
J01 | Relays/terminals | Interposing relay, 24 V DC coil, 1 CO, LED and test lever | Phoenix Contact | PLC-RSC-24DC/21 | 20 | 24 V DC | SCH-0202 | 2 wks | OK | Every DO leaving the board
J02 | Relays/terminals | Terminal, feed-through, 2.5 mm2, grey | Phoenix Contact | UT 2,5 | 360 | - | TRM-0401 | 2 wks | OK | Includes 20% spare
J03 | Relays/terminals | Terminal, feed-through, 4 mm2, grey | Phoenix Contact | UT 4 | 60 | - | TRM-0402 | 2 wks | OK | 240 V AC control
J04 | Relays/terminals | Terminal, DISCONNECT (knife), 2.5 mm2 | Phoenix Contact | UT 2,5-MT | 36 | - | TRM-0403 | 2 wks | OK | Every analogue loop - inject calibrator without unwiring
J05 | Relays/terminals | Terminal, feed-through, 2.5 mm2, YELLOW | Phoenix Contact | UT 2,5 YE | 24 | - | TRM-0404 | 3 wks | OK | SAFETY CIRCUIT ONLY. Includes 4 spare for future E-stop
J06 | Relays/terminals | Terminal, earth, 2.5 mm2 | Phoenix Contact | UT 2,5-PE | 40 | - | TRM | 2 wks | OK
J07 | Relays/terminals | Terminal, power, 35 mm2 | Phoenix Contact | UK 35 | 24 | - | TRM-0405 | 3 wks | OK | Small feeder outgoings
J08 | Relays/terminals | End covers, partition plates, end brackets, separators | Phoenix Contact | D-UT 2,5 / ATP / E-UK | 1 set | - | TRM | 2 wks | TBC | ROUTINELY UNDER-ORDERED. Quantity derived from rail layout. Partition plates REQUIRED between voltage groups. See DR-003
J09 | Relays/terminals | Terminal marker strips, printed | Phoenix Contact | ZB series | 1 set | - | TRM | 2 wks | OK | Printed FROM the termination schedule, not hand-written. See FD-006b
K01 | Wiring | Panel wire, tri-rated, 1.0 mm2, DARK BLUE - DC control | Generic BS6231 | - | 500 m | 0.6/1 kV | All | 2 wks | OK | AS 60204.1 colour convention
K02 | Wiring | Panel wire, tri-rated, 1.0 mm2, RED - AC control | Generic BS6231 | - | 200 m | 0.6/1 kV | All | 2 wks | OK
K03 | Wiring | Panel wire, tri-rated, 1.0 mm2, ORANGE - external source | Generic BS6231 | - | 50 m | 0.6/1 kV | SCH-0141 | 2 wks | OK | Conductors that stay LIVE when the board is isolated. Safety convention
K04 | Wiring | Panel wire, 2.5 / 4 / 16 / 35 / 95 mm2, black | Generic | - | Lot | 0.6/1 kV | All | 2 wks | OK | Power. 95 mm2 added at Rev D per CR-001
K05 | Wiring | Panel wire, green/yellow, 2.5 / 4 / 16 mm2 | Generic | - | Lot | - | All | 2 wks | OK | Earth
K06 | Wiring | Wire ferrules, printed, heat-shrink type | Partex / Grafoplast | - | Lot | - | All | 2 wks | OK | BOTH ends of every wire
K07 | Wiring | Slotted cable duct, 40x60 / 60x80 / 80x80, with lids | Betaduct / Panduit | - | Lot | - | GA-0020 | 3 wks | OK | SEPARATE ducts: power / AC control / DC digital / analogue
K08 | Wiring | DIN rail, 35 mm, slotted | Generic | - | Lot | - | GA-0020 | 2 wks | OK
K09 | Wiring | Bootlace ferrules, insulated, assorted | Generic | - | Lot | - | All | 2 wks | OK
K10 | Wiring | Crimp lugs, compression, for power terminations | Cabac / Utilux | Size to suit | Lot | - | TRM | 3 wks | TBC | Sizes depend on FINAL cable sizes. PO amended at CR-001 (70 to 95 mm2)
K11 | Wiring | Cable ties, spiral wrap, adhesive bases | Generic | - | Lot | - | - | 2 wks | OK
L01 | Labels | Traffolyte label, engraved, black on white, device labels | Local engraver | Per LBL-0001 | 140 | - | LBL-0001 | 3 wks | TBC | Cannot order until label schedule approved. MECHANICALLY FIXED, not adhesive
L02 | Labels | Traffolyte label, cubicle identification, large | Local engraver | Per LBL-0001 | 5 | - | LBL-0001 | 3 wks | TBC
L03 | Labels | Warning labels - danger 415 V, MULTIPLE SUPPLIES, CT secondary | Generic | Per LBL-0001 | Lot | - | LBL-0001 | 2 wks | OK | Multiple-supplies label added to schedule at Rev 1 - see FD-006c. CT secondary label is a genuine safety item
L04 | Labels | Asset / rating nameplate, engraved | Local engraver | Per LBL-0001 | 1 | - | LBL-0001 | 3 wks | TBC | Rated current, voltage, Icw, IP, mfr, date, standard - AS/NZS 61439 marking
L05 | Labels | Arc flash warning label | - | - | 1 | - | - | - | CLIENT SCOPE | Content comes from client arc flash study. We fit a blank holder only
M01 | Field | Local control station enclosure, GRP, IP66 | Schneider / Fibox | To suit XB5 devices | 2 | IP66 | LCS-0101/0102 | 4 wks | OK | Pump hall - wet, washdown
M02 | Field | LCS internals - L/R selector, Start, Stop, E-stop, Running lamp, terminals | Schneider Electric | Harmony XB5 range | 2 sets | 24 V DC | LCS-0101/0102 | 4 wks | OK
M03 | Field | RIO-01 enclosure, 316 stainless, IP66, 600 x 600 x 250 | Generic | - | 1 | IP66 | RIO-0001 | 6 wks | TBC | Outdoor at intake - confirm solar loading, sunshade or cooling
M04 | Field | RIO-01 internals - MCB, 24 V DC PSU, terminals, fibre LIU | Assorted | - | 1 set | - | RIO-0001 | 6 wks | TBC

## FAT Sheet
Test No. | Section | Test Description | Expected Result | Actual Result | Pass/Fail | Comments
A-01 | A Documentation | Drawing register complete, all drawings at listed revision | All present at Rev 1 | All present at Rev 1 | Pass
A-02 | A Documentation | BOM at current revision, reconciled against drawings | BOM Rev D reconciled | Reconciled | Pass
A-03 | A Documentation | Approved FAT procedure signed | Signed by client | Signed | Pass
A-04 | A Documentation | Equipment data sheets and test certificates available | All available | All available | Pass
A-05 | A Documentation | Manufacturer AS/NZS 61439 design verification evidence available | Documentation provided | Provided | Pass | Filed in MDR Section 6.1
A-06 | A Documentation | Calibration certificates for all test equipment, current | All current | All current | Pass
A-07 | A Documentation | PLC program version recorded | Version recorded | Recorded | Pass
A-08 | A Documentation | Outstanding items and deviations declared | Declared at FAT opening | Declared | Pass | Coordination study outstanding - declared up front
B-09 | B Visual inspection | Enclosure undamaged, paint finish acceptable | No damage | No damage | Pass
B-10 | B Visual inspection | Form of separation as specified (Form 3b) | Form 3b verified | Verified | Pass
B-11 | B Visual inspection | Equipment layout matches approved general arrangement | Matches GA Rev 1 | Matches | Pass
B-12 | B Visual inspection | All devices present and match BOM part numbers (labels physically read) | Match BOM Rev D | 1 discrepancy | FAIL | FD-002 KM103 240 V AC coil supplied instead of 24 V DC
B-13 | B Visual inspection | Labelling complete, engraved, mechanically fixed, matching drawings | All correct | 3 discrepancies | FAIL | FD-006
B-14 | B Visual inspection | Warning labels fitted including multiple supplies | All fitted | Multiple-supplies label missing | FAIL | FD-006c
B-15 | B Visual inspection | Asset / rating nameplate fitted and correct | Correct | Correct | Pass
B-16 | B Visual inspection | Board internally clean - no swarf, offcuts, packaging or tools | Clean | Clean | Pass
B-17 | B Visual inspection | Wiring workmanship - routing, duct fill, ferruling, consistency | Acceptable | Acceptable | Pass | Ferrule orientation corrected at 50% inspection
B-18 | B Visual inspection | Door wiring looms, service loops and strain relief | Correct | Correct | Pass
C-19 | C Mechanical inspection | Doors open, close and latch. Door interlocks operate | All correct | All correct | Pass
C-20 | C Mechanical inspection | Every isolating handle operates and padlocks in the off position | All operate and lock | All operate and lock | Pass
C-21 | C Mechanical inspection | Door interlock defeat mechanism operates and resets | Operates | Operates | Pass
C-22 | C Mechanical inspection | Removable items withdraw and re-insert correctly | Correct | Correct | Pass
C-23 | C Mechanical inspection | Gland plates removable, fixings complete | Correct | Correct | Pass
C-24 | C Mechanical inspection | Gaskets intact and continuous | Intact | Intact | Pass
C-25 | C Mechanical inspection | Lifting provisions secure and marked | Secure and marked | Secure and marked | Pass
C-26 | C Mechanical inspection | Terminal rails secure, end brackets fitted | Correct | Correct | Pass
D-27 | D Wiring verification | Point-to-point check of every internal wire against schematics (by a person other than the wireman) | All correct | 1 discrepancy | FAIL | FD-001 KT101 wired to NO contact instead of NC
D-28 | D Wiring verification | Wire numbers verified at both ends against drawings | All correct | All correct | Pass
D-29 | D Wiring verification | Terminal allocation verified against termination schedule | All correct | All correct | Pass
D-30 | D Wiring verification | Terminations tight - sample torque check, sample size recorded | Within spec | Within spec | Pass | 20% sample, all within manufacturer torque
D-31 | D Wiring verification | Conductor sizes per drawing | Correct | Correct | Pass
D-32 | D Wiring verification | Colour convention verified including orange for external supplies | Correct | Correct | Pass
D-33 | D Wiring verification | Maximum two conductors per terminal confirmed | Confirmed | Confirmed | Pass
E-34 | E Continuity and earth | Earth continuity, main earth bar to each cubicle earth bar, door, gland plate and equipment earth | Within client criterion, each reading recorded | All within criterion | Pass | Individual readings on attached sheet - not 'all satisfactory'
E-35 | E Continuity and earth | Instrument screen bar insulated from enclosure, bonded at ONE point only | > 1 Mohm to enclosure | 0 ohm | FAIL | FD-003 - mounting screw through to mounting plate
E-36 | E Continuity and earth | Continuity of every control circuit per schematic | All continuous | All continuous | Pass
E-37 | E Continuity and earth | Continuity from every field terminal to destination device | All continuous | All continuous | Pass
E-38 | E Continuity and earth | Phase continuity and identification through busbar to every feeder | Correct | Correct | Pass
F-39 | F Insulation resistance | ALL electronic equipment disconnected before IR test, per disconnection list, signed | Complete and signed | Complete and signed | Pass | Drives, PLC, PSUs, UPS, SPD, meter, electronic trip units
F-40 | F Insulation resistance | IR test power circuits - ph-ph, ph-N, ph-E, N-E | Per client criterion, readings recorded | All within criterion | Pass | Individual readings recorded
F-41 | F Insulation resistance | IR test control circuits (electronics disconnected) | Per client criterion | Within criterion | Pass
F-42 | F Insulation resistance | Every reading recorded individually | All recorded | All recorded | Pass
F-43 | F Insulation resistance | All disconnected equipment reconnected and verified - SIGNED step | Signed reconnection check | Complete and signed | Pass
G-44 | G Control power | Energise 240 V AC supply, verify voltage | Within tolerance | Within tolerance | Pass
G-45 | G Control power | Verify UPS operation, on-line status and status contacts | Correct | Correct | Pass
G-46 | G Control power | Energise PSU-1 with PSU-2 isolated, verify 24 V DC bus | Bus healthy | Bus healthy | Pass
G-47 | G Control power | Energise PSU-2 with PSU-1 isolated, verify 24 V DC bus | Bus healthy | Bus healthy | Pass
G-48 | G Control power | Both energised, verify redundancy module operation | Correct | Correct | Pass
G-49 | G Control power | Fail PSU-1 under load - no interruption to bus, alarm raised | Bus holds, alarm at SCADA | Bus holds, alarm at SCADA | Pass
G-49b | G Control power | Fail PSU-2 under load - no interruption to bus, alarm raised | Bus holds, alarm at SCADA | Bus holds, alarm at SCADA | Pass
G-50 | G Control power | Verify each ECP group live and correctly allocated | Correct allocation | Correct | Pass | Switch confirmed on ECP1 network group, not field I/O - DR-004
G-51 | G Control power | Trip one ECP group - only that group affected, status alarm raised | Group isolated, alarm raised | Correct | Pass
G-52 | G Control power | Verify PLC powers up, no faults, correct program version | No faults, version correct | Correct | Pass
G-53 | G Control power | Verify network switch and all network devices reachable | All reachable | All reachable | Pass
H-54 | H Functional testing | Lamp test - every indicator operates | All operate | All operate | Pass
H-55 | H Functional testing | Selector positions produce correct mode, PLC reads correct combination | Correct for all feeders | Correct | Pass | Both Local and Remote DIs read - Off detectable
H-56 | H Functional testing | Start and stop from MCC pushbuttons in Local | Correct | Correct | Pass
H-57 | H Functional testing | Start and stop from local control station in Local | Correct | Correct | Pass
H-58 | H Functional testing | Start and stop from PLC / SCADA in Remote | Correct | Correct | Pass
H-59 | H Functional testing | Local commands ignored in Remote and vice versa | Ignored | Ignored | Pass
H-60 | H Functional testing | Off position prevents all operation, PLC reports feeder unavailable | Correct | Correct | Pass
H-61 | H Functional testing | Running, fault and available indication at MCC and at LCS | Correct | Correct | Pass
H-62 | H Functional testing | DOL contactor pull-in and drop-out verified by CONTACTOR AUXILIARY, not PLC output | Aux confirms operation | Correct | Pass
H-63 | H Functional testing | Discrepancy alarms - commanded-but-not-running, running-but-not-commanded | Both operate | Both operate | Pass
H-64 | H Functional testing | Duty rotation logic - changeover on run hours | Correct | Correct | Pass
H-65 | H Functional testing | Duty / standby changeover on simulated duty pump fault | Correct | Correct | Pass
I-66a | I Interlocks and permissives | Remove thermistor permissive - start blocked, correct reason reported | Blocked, correct reason | Blocked, reason INCORRECT | FAIL | FD-004 alarm descriptions transposed
I-66b | I Interlocks and permissives | Remove drive healthy permissive - start blocked, correct reason | Blocked, correct reason | Correct | Pass
I-66c | I Interlocks and permissives | Remove low-low float permissive - start blocked, correct reason | Blocked, correct reason | Correct | Pass
I-66d | I Interlocks and permissives | Remove seal water permissive - start blocked, correct reason | Blocked, correct reason | Correct | Pass
I-66e | I Interlocks and permissives | Remove valve open permissive - start blocked, correct reason | Blocked, correct reason | Correct | Pass
I-66f | I Interlocks and permissives | Open Q11 - feeder unavailable, start blocked | Blocked | Correct | Pass
I-66g | I Interlocks and permissives | Press E-stop - start blocked | Blocked | Correct | Pass
I-66h | I Interlocks and permissives | Inject wet well level below setpoint - start blocked | Blocked | Correct | Pass
I-67 | I Interlocks and permissives | HARDWIRED dry-run trip operates with PLC in PROGRAM-STOP mode | Drive trips | Drive trips | Pass | CRITICAL TEST - the entire point of hardwiring it
I-68 | I Interlocks and permissives | Seal water start bypass timer operates then enforces permissive | Correct | Correct | Pass
I-69 | I Interlocks and permissives | HVAC-fail interlock ramps drives to minimum speed and alarms | Correct | Correct | Pass | TQ-005 outcome
J-70 | J Protection verification | Protection settings recorded against coordination study | Settings applied and verified | COORDINATION STUDY NOT AVAILABLE | N/A - DEVIATION | FD-005 - recorded as deviation, NOT as pass. SAT hold point
J-71 | J Protection verification | MPCB thermal settings verified against confirmed motor FLC | Correct | Correct | Pass
J-72 | J Protection verification | Drive motor thermal parameters verified against motor nameplate | Correct | Correct | Pass | 90 kW nameplate data per CR-001
J-73 | J Protection verification | Operate trip mechanism on each protective device, verify indication to PLC | All correct | All correct | Pass
J-74 | J Protection verification | Phase failure relay operates on simulated phase loss, alarm raised | Operates | Operates | Pass
J-75 | J Protection verification | SPD status contact reports correctly | Correct | Correct | Pass
J-76 | J Protection verification | CT shorting links present, CT secondary warning label fitted, meter reads correctly | All correct | All correct | Pass
K-77 | K PLC I/O simulation | Every digital input - operate field device, verify bit at PLC and tag at SCADA, description matches I/O list | All 40 correct | All 40 correct after FD-004 correction | Pass
K-78 | K PLC I/O simulation | Every digital output - force output, verify relay, field terminal and SCADA status | All 14 correct | All 14 correct | Pass
K-79 | K PLC I/O simulation | Every analogue input - inject 4, 8, 12, 16, 20 mA, verify EU at PLC and SCADA | All 6 correct at 5 points | All correct | Pass | 30 individual readings recorded
K-80 | K PLC I/O simulation | Every analogue output - command 0, 25, 50, 75, 100%, measure current at field terminal | Both correct | Both correct | Pass
K-81 | K PLC I/O simulation | Verify live-zero detection on each analogue input - open loop, fault detected and alarmed | All detect | All detect | Pass
K-82 | K PLC I/O simulation | Verify every spare I/O point terminated, labelled and available | All available | All available | Pass | 8 DI, 18 DO, 10 AI, 2 AO spare
K-83 | K PLC I/O simulation | Fail-safe check - disconnect critical DI field wire, signal reads FAULT not healthy | Reads fault | Reads fault | Pass
L-84 | L Alarm testing | Every alarm generated at source, verified at PLC and SCADA with correct description, priority and time stamp | All correct | 2 further description errors found | FAIL then Pass | FD-004 - full section re-run after correction, all correct
L-85 | L Alarm testing | Common alarm beacon and sounder operate | Operate | Operate | Pass
L-86 | L Alarm testing | Alarm acknowledge and reset behaviour | Correct | Correct | Pass
L-87 | L Alarm testing | Latched alarms remain latched until acknowledged | Correct | Correct | Pass
L-88 | L Alarm testing | Alarms that must survive a power interruption do so | Correct | Correct | Pass
M-89a | M Emergency stop | E-stop MCC door - both drives to STO, DOL contactors drop, alarm at SCADA | All operate | All operate | Pass
M-89b | M Emergency stop | E-stop LCS-101 - both drives to STO, contactors drop, alarm | All operate | All operate | Pass
M-89c | M Emergency stop | E-stop LCS-102 - both drives to STO, contactors drop, alarm | All operate | All operate | Pass
M-89d | M Emergency stop | E-stop pump hall - both drives to STO, contactors drop, alarm | All operate | All operate | Pass
M-90 | M Emergency stop | Plant cannot restart while E-stop latched | Cannot restart | Cannot restart | Pass
M-91 | M Emergency stop | Reset requires E-stop released AND reset button pressed and released | Correct | Correct | Pass
M-92 | M Emergency stop | Reset does NOT occur on press (monitored reset acts on release) | No reset on press | No reset on press | Pass
M-93a | M Emergency stop | SINGLE-CHANNEL FAULT - open channel A only, relay detects discrepancy, safe state, will not reset | Detected, will not reset | Detected, will not reset | Pass | The test that actually proves dual channel
M-93b | M Emergency stop | SINGLE-CHANNEL FAULT - open channel B only, relay detects discrepancy | Detected, will not reset | Detected, will not reset | Pass
M-94 | M Emergency stop | Safety relay auxiliary status reaches PLC and SCADA | Correct | Correct | Pass
M-95 | M Emergency stop | E-stop function with PLC in PROGRAM-STOP - safety function independent of PLC | Operates | Operates | Pass
N-96 | N Local / remote | Mode logic recorded per feeder | All recorded | All recorded | Pass
N-97 | N Local / remote | ALL permissives and trips remain active in Local mode | All active | All active | Pass | Design decision verified - Local does not bypass protection
O-98 | O VSD operation | Motor simulation method per agreed arrangement | Per agreed method | Test motor, no load | Pass | Method agreed with client in advance
O-99 | O VSD operation | Drive parameters verified against parameter schedule, full set backed up | Verified and backed up | Verified and backed up | Pass | Backup files to MDR Section 5.3
O-100 | O VSD operation | Run command, start, ramp, stop, ramp-down | Correct | Correct | Pass
O-101 | O VSD operation | Speed reference tracking at 0 / 25 / 50 / 75 / 100 % | Within tolerance | Within tolerance | Pass | Test motor, no load - does NOT prove performance under load
O-102 | O VSD operation | Minimum and maximum speed clamps | Correct | Correct | Pass
O-103 | O VSD operation | Acceleration and deceleration ramp times | Per parameter schedule | Correct | Pass
O-104 | O VSD operation | STO operation from safety relay, both channels | Correct | Correct | Pass | STO terminals re-verified after CR-001 drive change
O-105 | O VSD operation | Drive fault, healthy and running signals via hardwired AND network routes | Both routes correct | Both correct | Pass
O-106 | O VSD operation | Live-zero response on loss of speed reference | Holds last speed and alarms | Correct | Pass | Configured response, not default
O-107 | O VSD operation | Motor thermal parameters and external thermistor trip input | Correct | Correct | Pass | Retested after FD-001 rectification
P-108 | P Network | Every network device reachable at assigned IP address | All reachable | All reachable | Pass
P-109 | P Network | Address schedule matches issued IP schedule | Matches | Matches | Pass
P-110 | P Network | Fibre links - light levels within specification | Within spec | Within spec | Pass
P-111 | P Network | Switch configuration - VLANs, port settings, management access | Correct | Correct | Pass
P-112 | P Network | Drive data over EtherNet/IP - status, speed, current, fault codes | All correct | All correct | Pass
P-113 | P Network | Power meter data | Correct | Correct | Pass
P-114 | P Network | Remote I/O node communication and every RIO point | All correct | All correct | Pass | 12 RIO points verified
P-115 | P Network | NETWORK FAILURE - disconnect network, hardwired control still functions, comms-fail alarm raised | Control retained, alarm raised | Control retained, alarm raised | Pass | Validates the hardwired control design decision
Q-116 | Q Labels | Every label checked against label schedule, character for character | All match | 3 discrepancies | FAIL | FD-006
Q-117 | Q Labels | Asset / rating nameplate content per AS/NZS 61439 marking requirements | Correct | Correct | Pass
Q-118 | Q Labels | Terminal markers checked against termination schedule | All correct | 2 markers transposed on X3 | FAIL | FD-006b
Q-119 | Q Labels | Warning labels present and correct | All present | Multiple-supplies label missing | FAIL | FD-006c
Q-120 | Q Labels | Arc flash label holder present (content client scope) | Holder present | Holder present | Pass
R-121 | R Drawing mark-ups | Every discrepancy marked on drawings in red AS FOUND, not reconstructed | All marked as found | All marked as found | Pass
R-122 | R Drawing mark-ups | Marked-up drawings signed and dated by the person who marked them | Signed and dated | Signed and dated | Pass
R-123 | R Drawing mark-ups | Marked-up set retained as basis for as-built drawings | Retained | Retained | Pass
S-124 | S Punch list | Every defect recorded with category, owner, action and due date | All recorded | All recorded | Pass | 8 items
S-125 | S Punch list | Categories agreed with client BEFORE FAT started | Agreed | Agreed | Pass
S-126 | S Punch list | Punch list signed by both parties at close of FAT | Signed | Signed | Pass
S-127 | S Punch list | Retest requirements identified and agreed at the time of each defect | Agreed at the time | Agreed at the time | Pass

## Punch List
Item | Description | Category | Raised By | Owner | Action | Retest Required | Due | Status | Engineering Approval | Drawing/BOM Revision
FD-001 | KT101 thermistor relay contact wired NO instead of NC - motor over-temperature protection would never operate | A | PE | Workshop | Rewire to NC contact | D-27 (circuit), I-66a, O-107 | FAT Day 1 | Closed | Not required - schematic was correct | None
FD-002 | KM103 fitted with 240 V AC coil instead of 24 V DC (LC1D09P7 vs LC1D09BD). Risk of 240 V being introduced into ELV wiring | A | PE | Workshop | Replace; physically verify ALL coils in board (1 further error found) | D-27, H-56 to H-63, I-66 for that feeder | FAT Day 1 | Closed | Not required - BOM was correct | None
FD-003 | Instrument screen earth bar bonded to enclosure at multiple points - single-point design defeated | B | PE | Workshop | Fit correct insulating hardware, re-verify, confirm single-point bond | E-35 plus re-check every screen termination | FAT Day 2 | Closed | Not required | GA-0020 annotated with screen bar mounting detail
FD-004 | SCADA alarm descriptions transposed - thermistor trip reported as seal water fail | B | Client | Integrator | Correct program; re-verify EVERY alarm description against I/O list (2 further errors found) | Full Section L re-run | FAT Day 2 | Closed | Not required - I/O list was correct | None
FD-005 | Protection coordination study not available - adjustable device settings cannot be verified. Discrimination unverified | DEVIATION | PE | CLIENT | Provide study; apply and verify settings on site. Provisional settings recorded and labelled inside board | J-70 at SAT | SAT HOLD POINT | OPEN - carried forward | YES - client written acceptance required for dispatch | Settings sheet marked PROVISIONAL
FD-006a | Door label reads P101, drawing says P-101 | C | Client | Workshop | Re-engrave | Q-116 | FAT Day 3 | Closed | Not required | None
FD-006b | X3 terminal marker strip - two markers transposed. Will cause future wiring errors | B | PE | Workshop | Reprint markers FROM the termination schedule | Q-118 | FAT Day 2 | Closed | Not required | None
FD-006c | Multiple-supplies warning label missing. Board contains externally-sourced live conductors at MOV-101 interface | B | PE | Workshop | Fit label AND add to label schedule (root cause was a schedule omission) | Q-119 | FAT Day 2 | Closed | Not required | LBL-0001 revised

## Inspection Checklist
Ref | Group | Check | Inspection Point | Result | Comment
1.1 | ENCLOSURE | Dimensions match approved GA | 1 Enclosure
1.2 | ENCLOSURE | Form of separation as specified (Form 3b) | 1 Enclosure
1.3 | ENCLOSURE | Doors align, close, latch correctly | 1 Enclosure
1.4 | ENCLOSURE | Gaskets continuous and undamaged at corners | 1 Enclosure
1.5 | ENCLOSURE | Gland plates removable, undrilled, non-magnetic | 1 Enclosure
1.6 | ENCLOSURE | Main earth bar full length and accessible | 1 Enclosure
1.7 | ENCLOSURE | Instrument screen bar insulated, single-point bonded | 1 Enclosure
1.8 | ENCLOSURE | Paint finish and colour correct, no damage | 1 Enclosure
1.9 | ENCLOSURE | Lifting provisions adequate and marked | 1 Enclosure
1.10 | ENCLOSURE | Ventilation and filters as designed | 1 Enclosure
2.1 | LAYOUT | Devices match BOM part numbers - labels physically read | 2 Pre-wire
2.2 | LAYOUT | Manufacturer clearances respected, especially around drives | 2 Pre-wire
2.3 | LAYOUT | Device orientation correct per manufacturer | 2 Pre-wire
2.4 | LAYOUT | Heat-generating devices not below heat-sensitive devices | 2 Pre-wire
2.5 | LAYOUT | Adjustable devices reachable without removing other equipment | 2 Pre-wire
2.6 | LAYOUT | Readable devices at sensible height (800-1800 mm) | 2 Pre-wire
2.7 | LAYOUT | Replaceable items removable in situ | 2 Pre-wire
2.8 | LAYOUT | Voltage zone segregation maintained by layout | 2 Pre-wire
2.9 | LAYOUT | Spare chassis space usable, not an awkward gap | 2 Pre-wire
3.1 | WIRING | Wire size and type per drawing | 3 50% wire and 4 Pre-FAT
3.2 | WIRING | Colour convention applied including ORANGE for external supplies | 3 50% wire and 4 Pre-FAT
3.3 | WIRING | Every wire ferruled BOTH ends, numbers match drawings | 3 50% wire and 4 Pre-FAT
3.4 | WIRING | Ferrules readable in situ, consistent orientation | 3 50% wire and 4 Pre-FAT
3.5 | WIRING | Duct fill leaves room for lid and future additions | 3 50% wire and 4 Pre-FAT
3.6 | WIRING | Power / AC control / DC digital / analogue in SEPARATE ducts | 3 50% wire and 4 Pre-FAT
3.7 | WIRING | Door wiring in flexible loom, service loop, strain relief both ends | 3 50% wire and 4 Pre-FAT
3.8 | WIRING | Terminations tight, torqued where specified | 3 50% wire and 4 Pre-FAT
3.9 | WIRING | Bootlace ferrules on stranded conductors | 3 50% wire and 4 Pre-FAT
3.10 | WIRING | Maximum 2 conductors per terminal and terminal rated for it | 3 50% wire and 4 Pre-FAT
3.11 | WIRING | Screens terminated per design (1 end instrument / 360 deg both ends VSD) | 3 50% wire and 4 Pre-FAT
3.12 | WIRING | No sharp edges against wiring, penetrations protected | 3 50% wire and 4 Pre-FAT
3.13 | WIRING | Adequate slack at terminals for re-termination | 3 50% wire and 4 Pre-FAT
4.1 | TERMINALS | Rails as designed, in designed order | 3 50% wire and 4 Pre-FAT
4.2 | TERMINALS | Numbering matches termination schedule | 3 50% wire and 4 Pre-FAT
4.3 | TERMINALS | Partition plates fitted between voltage groups | 3 50% wire and 4 Pre-FAT
4.4 | TERMINALS | End brackets and end covers fitted | 3 50% wire and 4 Pre-FAT
4.5 | TERMINALS | Marker strips printed FROM schedule, not hand-written | 3 50% wire and 4 Pre-FAT
4.6 | TERMINALS | Spare terminals fitted, labelled SPARE, grouped | 3 50% wire and 4 Pre-FAT
4.7 | TERMINALS | Yellow terminals used for safety circuit ONLY | 3 50% wire and 4 Pre-FAT
4.8 | TERMINALS | Disconnect terminals on every analogue loop | 3 50% wire and 4 Pre-FAT
4.9 | TERMINALS | Field access adequate for gloved hand and screwdriver | 3 50% wire and 4 Pre-FAT
5.1 | LABELS | Every device labelled with drawing tag | 4 Pre-FAT
5.2 | LABELS | Engraved traffolyte, mechanically fixed (not adhesive) | 4 Pre-FAT
5.3 | LABELS | Text matches drawings character for character | 4 Pre-FAT
5.4 | LABELS | Cubicle identification labels fitted | 4 Pre-FAT
5.5 | LABELS | Warning labels: 415 V, MULTIPLE SUPPLIES, CT secondary | 4 Pre-FAT
5.6 | LABELS | Asset / rating nameplate fitted and correct | 4 Pre-FAT
5.7 | LABELS | Arc flash label holder fitted | 4 Pre-FAT
6.1 | EARTHING | Main earth bar continuous and correctly sized | 3 50% wire and 4 Pre-FAT
6.2 | EARTHING | Cubicle earth bars bonded to main bar | 3 50% wire and 4 Pre-FAT
6.3 | EARTHING | Every equipment-bearing door bonded with flexible strap | 3 50% wire and 4 Pre-FAT
6.4 | EARTHING | Gland plates bonded | 3 50% wire and 4 Pre-FAT
6.5 | EARTHING | All equipment earths present | 3 50% wire and 4 Pre-FAT
6.6 | EARTHING | PAINT REMOVED / serrated washers at EVERY bonding point | 3 50% wire and 4 Pre-FAT
6.7 | EARTHING | Screen bar insulated, bonded at one point only | 3 50% wire and 4 Pre-FAT
7.1 | DOCUMENT CONTROL | Drawings on bench are CURRENT IFC revision | ALL four points
7.2 | DOCUMENT CONTROL | Superseded drawings physically removed from workshop | ALL four points
7.3 | DOCUMENT CONTROL | Workshop mark-ups captured for as-built | ALL four points
7.4 | DOCUMENT CONTROL | Any changes have been through change control | ALL four points
8.1 | GENERAL | Board clean - no swarf, offcuts or tools inside | 4 Pre-FAT
8.2 | GENERAL | Packing, transit restraints and desiccant identified for removal | 4 Pre-FAT
8.3 | GENERAL | Spares and loose items bagged, labelled and listed | 4 Pre-FAT

## MDR Index
Section | Document | Document Number | Rev | Originator | Status | Notes
1.2 | Document index | NFD-ELE-MDR-0001 | 0 | PE | Included
1.3 | Equipment register with serial numbers | NFD-ELE-EQR-0001 | 0 | Workshop | Included
2.1 | Design basis | NFD-ELE-DBS-0001 | 1 | Designer / PE | Included
2.2 | Design input register | NFD-ELE-REG-0001 | 1 | PE | Included | Closed out, open items flagged
2.3 | Assumptions register | NFD-ELE-REG-0002 | 1 | PE | Included | MOST OFTEN OMITTED, MOST OFTEN NEEDED
2.4 | Functional description | NFD-ELE-FDS-0001 | 1 | PE | Included
2.6 | I/O list | NFD-ELE-IOL-0001 | 1 | Designer | Included
2.7 | Load schedule | NFD-ELE-LSC-0001 | 1 | Designer | Included
2.8 | Interface register | NFD-ELE-IFR-0001 | 1 | PE | Included
3.1 | Drawing register with revision history | NFD-ELE-DRG-0001 | 1 | PE | Included
3.2 | Single line diagram | NFD-ELE-SLD-0001 | 1 | Designer | Included
3.3 | General arrangement and cubicle layouts | NFD-ELE-GA-0020 | 1 | Designer | Included
3.4 | Schematic diagrams - all sheets | NFD-ELE-SCH-00xx | 1 | Designer | Included
3.5 | Termination drawings and schedule | NFD-ELE-TRM-04xx | 1 | Designer | Included
3.6 | Cable schedule | NFD-ELE-CBS-0001 | 1 | Designer | Included | Sizes provisional - see CF-08
3.7 | Label schedule | NFD-ELE-LBL-0001 | 1 | Designer | Included
3.10 | Network architecture drawing | NFD-ELE-SCH-0301 | 1 | Designer | Included
4.1 | As-built drawing set | NFD-ELE-xxx-AB | AS-BUILT | Designer / PE | Included | PHYSICALLY VERIFIED against the board, not transcribed
4.3 | Record of differences between approved and as-built sets | NFD-ELE-ABD-0001 | 0 | PE | Included
5.1 | Final BOM, as-built, reconciled | NFD-ELE-BOM-0001 | D | PE | Included
5.2 | Equipment data sheets | Vendor | - | Vendors | Included
5.3 | Drive parameter schedule + backup FILES | NFD-ELE-PAR-0001 | 0 | Workshop / integrator | Included | Files, not printouts
5.4 | Protection settings schedule, as applied | NFD-ELE-PRS-0001 | 0 | PE | Included | MARKED PROVISIONAL - see CF-01
5.5 | Spares list and recommended spares holding | NFD-ELE-SPR-0001 | 0 | PE | Included
6.1 | Manufacturer AS/NZS 61439 design verification evidence | Manufacturer | - | Panel builder | Obtained | MANUFACTURER responsibility, not designer
6.2 | Manufacturer routine verification records | Manufacturer | - | Panel builder | Obtained
6.3 | Equipment type test certificates and compliance declarations | Vendor | - | Vendors | Obtained | Chased BEFORE final payment
6.5 | Calibration certificates for FAT test equipment | Various | - | Workshop | Included
7.1 | Approved FAT procedure | NFD-ELE-FAT-0001 | 1 | PE | Included
7.2 | Completed FAT sheet, signed, all actual results | NFD-ELE-FAT-0001 | 1 | PE / Client | Included | 127 tests, individual results
7.3 | Earth continuity test results - individual readings | FAT attachment | - | Workshop | Included | Not 'all satisfactory'
7.4 | Insulation resistance test results - individual readings | FAT attachment | - | Workshop | Included
7.7 | Emergency stop test records incl. single-channel fault tests | FAT attachment | - | Workshop | Included
7.9 | Retest records for every punch-list item | FAT attachment | - | PE | Included
8.1 | In-progress inspection records - all four inspection points | NFD-ELE-INS-0001 | - | PE | Included
8.2 | Goods-inward inspection records | Workshop | - | Workshop | Included | Root cause of FD-002
9.1 | Technical query register with responses | NFD-ELE-TQR-0001 | - | PE | Included | Open items flagged
9.2 | Deviation register with client written acceptances | NFD-ELE-DEV-0001 | - | PE | Included | DEV-002 explains the drive brand decision
9.3 | Change register with impact assessments and approvals | NFD-ELE-CHG-0001 | - | PE | Included | CR-001 motor uprate
10.1 | VSD manuals - installation, programming, maintenance | Danfoss | - | Vendor | Included
10.2 | PLC and I/O manuals | Rockwell | - | Vendor | Included
10.3 | Network equipment manuals and configuration backup | Moxa | - | Vendor | Included
10.6 | Safety relay manual | Pilz | - | Vendor | Included
11.1 | Final punch list with close-out evidence | NFD-ELE-PCH-0001 | 1 | PE / Client | Included
11.2 | ITEMS CARRIED FORWARD TO SITE | NFD-ELE-CF-0001 | 0 | PE | Included | SIGNED BY BOTH PARTIES - 10 items
11.4 | Close-out certificate | NFD-ELE-COC-0001 | 0 | PE / Client | Included
12.3 | Settings to be applied before energisation | Within CF-0001 | 0 | PE | Included | Protection settings hold point
12.5 | KNOWN LIMITATIONS OF THE FAT | Within FAT report | 1 | PE | Included | EXPLICIT - what was simulated and what was not
12.7 | Spare capacity record | NFD-ELE-SPC-0001 | 0 | PE | Included | Written unprompted